## Cleaning
Item: | Cleaning plant for cleaning the exhaust gases
Scope: | The supply includes: designing (design must be confirmed by the inverstor) manufgacturing, installation, test run, training and handing over of the fully operational system.
Operational parameters
gases to clean: | mainly exhaust gases, arising form fire tests done in furnasec fired with oil
fuel for furnaces: | oil (process heat), from the testing: wood, mineral wool, PIR, PUR, PE, PP, PVC
estimated expected flow through the system | minimum 90.000 m3/h at 300 oC
Maximum allowed total electrcal power due to grid limitations | 380 kW
expected inlet temperature: | Depending on the burning process, possibly up to 850 °C; Technical solutions for cooling the inlet gases if neccesary must be part of the cleaning system.
installation and plot: | outdoor installation, available area approx 6 m by 17 m, the plant may be up to 15 m high above the ground level (excluding exhaust), exhaust minimum 18 m and maximum 23 m tall
the cleaning plant must be connectable to multiple sources: | two fire resistance furnaces (EN 1363), ventilation system for room corner test (ISO 9705) and façade testing/calorimeter (ISO 24473), as well as an SBI test (EN 13823)
required cleaning levels
General: | The cleaned exhaust waste gas should comply to German TI-Air (TA-Luft)
- particles and dust content in the exhaust: | < 20 mg/m3
- SO2 | < 50 mg/m3
- HCl | < 10 mg/m3
- HF | < 3 mg/m3
Modularity | The system and its configuration must enable later addition or extension of the plant, providing otherwise not expected pollutants (like PCDD/PCDF i.e. Dioxins and Furans), if required.
it is mandatory that the system is built in close cooperation with the chosen furnaces provider to adjust the design if neccesary. Special care must be given not to adversley affexct furnace pressure control (see EN 1363-1) or SBI volume flow (0,6 +- 0,05 m3/s, see EN 13823)..
notes: | the design of the building is available for download, position of the cleaning plant is marked.
http://www.zag.si/dl/logatec/1_nacrt_arhitekture.zip

## Čiščenje
Predmet: | Čistilna naprava za čiščenje dimnih plinov
Obseg | Dobava obsega: izdelavo načrta / sheme (načrt mora potrditi naročnik), izdelavo naprave, montažo naprave, zagon naprave, šolanje in prevzem polno delujoče naprave
Paramteri delovanja
Dimni plini, ki jih je potrebno očistitit | večinoma plini, ki nastajjao pri preskušanju požarnih lastnosti gradbenih konstrukcij v peči z gorivom ELKO
Gorivo peči | ELKO (primarno gorivo), preskušanci: mineralna volna, PIR, PUR, PE, PP, PVC
Pričakovana kapaciteta sistema | minimamalno 90.000 m3/h pri 300 oC
Najvišja dovoljena prikljućna elektirčna moč, zaradi omejitve elektičnih inštalacij | 380 kW
Pričakovana temperatura na vhodu v čistilno napravo | Odvisno od procesa gorenja, do 850 °C; tehnična rešitev hlajenja plinov pred vstopom v napravo, če je to potrebno, je del ponujenega sistema.
Namestitev in tloris | Zunanja namestitev na površino največ 6 m x 17 m, naprava je lahko visoka do 15 m od tal (brez dimnika), dimnik najmanj 18 m in največ 23 m od tal.
Čistilna naprava mora omogočati priklop različnih virov | najmanj dve peči pa preskušanje požarne odpornosti (EN 1363), ventilacijski sistem za room-corner test (ISO 9705) in fasandno preskuševališče / odptri kalorimeter (ISO 24473), kot tudi za SBI test (EN 13823)
Zahtevano čiščenje
Splošno | Očiščeni dimni plini morajo dosegati zahteve nemškega TI-Air (TA-Luft)
- delci in prah v izpustih iz peči: | < 20 mg/m3
- SO2 | < 50 mg/m3
- HCl | < 10 mg/m3
- HF | < 3 mg/m3
Modularnost | Sistem mora omogočati morebitno nadgradnjo za čiščenje komponent, ki jih sicer ne pričakujemo, npr. PCDD/PCDF (diksini in furani), ki jih sicer ne pričakujemo.
dobavitelj sistema se mora pri načrtovanju naprave obvezno usklajevati z izbranim dobaviteljem peči. Posebno skrb je treba posvetiti vplivu sistema na tlak v preskusnih pečeh (glej EN 1363-1) ali pretok SBI (0,6 +- 0,05 m3/s, glej EN 13823).
Opomba | Na voljo so načrti stavbe za umeščanje čistilne naprave z označeno lokacijo čistilne naprave.
http://www.zag.si/dl/logatec/1_nacrt_arhitekture.zip