Technical specification for Items No. 153850

1. SCOPE Line; NEK Item Number; Part Number; UOM; Quantity; Need by Date; Safety Classification. 1; 422820; 3154ND2R2F4E8C3D3Q8Q9R1+QDC1A1W2C000; EA; 7; 1-Jul-22; SR. TRANSMITTER.ELECTRIC,SC:SR,TYPE:DIFFERENTIAL PRESSURE,RANGE:-250 to 250 inH2O,HOUSING:SST,MODEL:3154ND,NOTE:EGS QDC CONNECTOR ASSEMBLED TO TRANSMITTER. MFG: ROSEMOUNT INC, United States Item shall be supplied in accordance with the following TQRs: A00, A02, A07, B00, B01, B04, B06, B08, C00, C01, F00, F02, F40, F50, F51, F521, F57, F59, F90, G00, G01 The following documents and/or records shall be submitted with the above item: G05 - CERTIFICATE OF COMPLIANCE WITH PURCHASE ORDER REQUIREMENTS G10 - CERTIFICATE OF COMPLIANCE TO IEEE 323/344 G22 - NONCONFORMANCE REPORTS G52 - CALIBRATION TEST RECORD G53 - EQUIPMENT/ITEM QUALIFICATION TEST REPORT (EQTR) G80 - MATERIAL CERTIFICATE (CHEMICAL COMPOSITION AND MECHANICAL PROPERTIES) I13 - EMI/RFI QUALIFICATION X100 - EQ EQUIPMENT.

2. TECHNICAL AND QUALITY REQUIREMENTS IMPORTANT: The quotation has to include Statement of Compliance with the following Technical and Quality Requirements. If any of these requirements could not be fulfilled, state the explanation

A00 - GENERAL REQUIREMENTS ALL REQUIRED DOCUMENTS SHALL BE SUPPLIED IN ENGLISH OR ENGLISH/ MULTILINGUAL. A02 - ORDER ENTRY REQUIREMENTS THE SALES OFFICE AND/OR IMPORTER RECEIVING THIS PURCHASE ORDER SHALL TRANSMIT ALL NEK PURCHASE ORDER REQUIREMENTS TO THE EQUIPMENT MANUFACTURER.. A07 - NEW ITEMS ALL ITEM(S) PROVIDED ON THIS PURCHASE ORDER SHALL BE SUPPLIED IN THE NEW CONDITION (NOT USED OR REFURBISHED IN ANY WAY)....

B00 - QUALITY ASSURANCE REQUIREMENTS B01 - QUALITY ASSURANCE PROGRAM ALL SERVICES AND ITEMS, INCLUDING THOSE WHICH HAVE TO COMPLY WITH ASME CODE REQUIREMENTS, SHALL BE PERFORMED/ PROVIDED IN ACCORDANCE WITH A QUALITY ASSURANCE PROGRAM THAT COMPLIES WITH 10CFR50 APPENDIX B, ANSI N45.2-1977 OR ASME NQA-1, AND HAS BEEN PREVIOUSLY EVALUATED AND ACCEPTED BY NEK.. B04 - SUPPLIER QA MANUAL CONTROLLED DISTRIBUTION IF A CONTROLLED COPY OF THE LATEST REVISION OF THE SUPPLIER'S QUALITY ASSURANCE PROGRAM MANUAL HAS NOT BEEN PREVIOUSLY SENT TO NEK, SUBMIT A COPY OF THIS DOCUMENT TO: DARKO KAVŠEK, QUALITY & NUCLEAR OVERSIGHT DIRECTOR tel.:++386 748 02 429 E-mail:darko.kavsek@nek.si IF A REVISION TO THE SUPPLIER'S QUALITY ASSURANCE MANUAL IS MADE DURING THE CONDUCT OF WORK ASSOCIATED WITH THIS ORDER, A COPY OF THE REVISION SHALL BE SUBMITTED TO THE ABOVE ADDRESS PRIOR TO IMPLEMENTATION OF THE CHANGE.. B06 - 10CFR21 REPORTING THIS ORDER IS SUBJECT THE PROVISIONS OF THE TITLE 10 OF THE U.S. CODE OF FEDERAL REGULATIONS PART 21, REPORTING OF DEFECTS AND NONCOMPLIANCE, REPORTING PURSUANT TO 10CFR21 SHALL BE MADE TO: ZVONIMIR ZEC , ENGINEERING SUPPORT FOR LONG TERM OPERATION SUPERINTENDENT tel:++386 748 02 262 E-MAIL: zvonimir.zec@nek.si. B08 - RETENTION OF RECORDS A RECORD SYSTEM (RETENTION TIME FOR LIFETIME AND NON-PERMANENT RECORDS) SHALL BE ESTABLISHED AND MAINTAINED BY THE SUPPLIER THAT PROVIDES DOCUMENTARY EVIDENCE OF THE QUALITY OF THE ITEMS AND ACTIVITIES AFFECTING QUALITY. THESE QA RECORDS SHALL INCLUDE RESULTS OF REVIEWS, INSPECTIONS,TESTS, AUDITS, MONITORING OF WORK PERFORMANCE AND MATERIAL ANALYSIS. RECORDS SHALL, AS A MINIMUM, IDENTIFY THE INSPECTOR OR DATA RECORDER, DATE INSPECTION WAS PERFORMED, TYPE OF OBSERVATION, PROCEDURES USED, RESULTS, ACCEPTABILITY, AND ACTION TAKEN FOR DEFICIENCIES NOTED. ADDITIONAL RECORDS OF SUPPORTING DATA SHALL ALSO BE MAINTAINED. ALL QUALITY VERIFICATION RECORDS, PROCEDURES AND QUALIFICATIONS SHALL BE IDENTIFIABLE TO THE ITEM OR ACTIVITY INVOLVED. THESE RECORDS SHALL BE RETRIVEABLE AND AVAILABLE FOR EXAMINATION. THE CLASSIFICATION AND RETENTION TIME OF LIFETIME AND NON-PERMANENT RECORDS SHALL BE IN COMPLIANCE WITH THE REQUIREMENTS OF USNRC REGULATORY GUIDE 1.28, REV. 3-1985. THE SUPPLIER MAY DISPOSE OF NON-PERMANENT RECORDS AFTER THE REQUIRED RETENTION PERIOD. IF THE SUPPLIER GOES OUT OF BUSINESS BEFORE THE END OF THE RETENTION PERIOD OF THESE RECORDS, THE SUPPLIER WILL SEND ONE COPY OF THESE RECORDS TO THE NEK IMPORT DEPARTMENT SUPERINTENDENT....

C00 - NONCONFORMANCE AND DEVIATION C01 - NO SUBSTITUTIONS THE SUPPLIER SHALL NOT SUBSTITUTE OTHER ITEMS FOR THE ITEMS REQUESTED WITHOUT SPECIFIC WRITTEN APPROVAL OF NEK PRIOR TO SHIPMENT. IF THE SUPPLIER IDENTIFIES CHANGES,NONCONFORMANCES, OR SEEKS WAIVERS FROM OTHER REQUIREMENTS OF THIS PURCHASE ORDER, THE SUPPLIER SHALL DESCRIBE SUCH CONDITIONS AND THIS INFORMATION SHALL BE TRANSMITTED, IN WRITING, TO NEK IMPORT DEPARTMENT SUPERINTENDENT. IF THE REQUESTED INFORMATION IS APPROVED BY NEK, THE SUPPLIER SHALL INCLUDE AN APPROVED COPY OF THE INFORMATION STATEMENT WITH THE ITEMS SHIPPED. THE SUPPLIER SHALL IDENTIFY ANY CHANGE MADE TO UPGRADE ANY ITEM ON THIS PURCHASE ORDER AS A RESULT OF USNRC CORRESPONDENCE (SUCH AS INFORMATION NOTICES, BULLETINS AND ADVISORY LETTERS). CHANGES AS PART OF THE SUPPLIER'S PRODUCT IMPROVEMENT PROGRAM SHALL ALSO BE IDENTIFIED AND TRANSMITTED IN WRITTING TO THE NEK IMPORT DEPARTMENT SUPERINTENDENT FOR APPROVAL....

F00 - SHIPPING, HANDLING, MARKING AND STORAGE INSTRUCTIONS F02 - HANDLING, PACKAGING AND SHIPPING HANDLING, PACKAGING AND SHIPPING OF THE ITEM SUPPLIED UNDER THIS PURCHASE ORDER SHALL BE IN ACCORDANCE WITH AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI) N45.2.2-LEVEL B.. F40 - SUPPLIER'S NAME. F50 - ITEM MARKING REQUIREMENTS ALL ITEMS ARE TO BE PACKAGED INDIVIDUALLY AND IDENTIFIED WITH THE SPECIFIC PART NUMBER, OR ALL ITEMS OF A GIVEN PART NUMBER TO BE PACKAGED TOGETHER AND IDENTIFIED WITH THE SPECIFIC PART NUMBER AND THE FOLLOWING:. F51 - THE PURCHASE ORDER NUMBER. F521 - PART/ CATALOG NO.. F57 - MANUFACTURER'S NAME. F59 - ITEM SERIAL NUMBER. F90 - PACKING SLIPS ARE TO BE SHIPPED WITH ORDER...

G00 - SUPPLIER DOCUMENTATION REQUIREMENTS ALL REQUIRED DOCUMENTS SHALL BE SUPPLIED IN ORIGINAL HARD COPY OR ELECTRONIC FORM DEFINED BY SUPPLIER QA PROGRAM AND ACCEPTED BY NEK. G01 - DOCUMENT TRACEABILITY ALL REQUIRED DOCUMENTS SHALL BE TRACEABLE TO THE NEK PURCHASE ORDER. DOCUMENTS SUPPLIED WHICH ARE ASSOCIATED WITH SPECIFIC ITEMS ON THE ORDER, SUCH AS TEST REPORTS, SHALL BE IDENTIFIED IN ORDER TO ESTABLISH TRACEABILITY TO THAT ITEM OR GROUP OF ITEMS.. G05 - CERTIFICATE OF COMPLIANCE WITH PURCHASE ORDER REQUIREMENTS THE CERTIFICATE OF COMPLIANCE SHALL SATISFY THE FOLLOWING CRITERIA: 1. IDENTIFY THE PURCHASE ORDER NUMBER, INCLUDING ITEM NUMBERS AND CHANGE ORDER NUMBER APPLICABLE TO THE ITEM BEING CERTIFIED. 2. A PERSON IDENTIFIED IN THE SUPPLIER'S QUALITY ASSURANCE PROGRAM DESCRIPTION AS RESPONSIBLE FOR CERTIFICATION SHALL ATTEST TO THE CERTIFICATE BY SIGNATURE, TITLE AND DATE OF SIGNING. 3. SUPPORTING DOCUMENTATION TO SUBSTANTIATE THE CERTIFICATE SHALL BE INCLUDED, UNLESS OTHERWISE WAIVED BY NEK. 4. NEK RESERVES THE RIGHT TO DETERMINE THE VALIDITY OF THE CERTIFICATE OF COMPLIANCE BY AN AUDIT OF THE SUPPLIER OR BY AN INSPECTION OR TEST OF THE ITEM(S).. G10 - CERTIFICATE OF COMPLIANCE TO IEEE 323/344 THE SUPPLIER SHALL PROVIDE A CERTIFICATION SHOWING THE ITEM(S) HAS BEEN QUALIFIED IN ACCORDANCE WITH IEEE 323-1974, IEEE 344-1975 AND THE ENVIRONMENTAL CODITION OF THE ORDER AS APPLICABLE.. G22 - NONCONFORMANCE REPORTS THE SUPPLIER SHALL PROVIDE A COPY OF ALL NONCONFORMANCE REPORTS AS REPAIR OR USE-AS-IS DISPOSITION OF MATERIALS DURING THE MANUFACTURING PROCESS TO UTILITIES ONLY IN CASES THAT AFFECT ENVIRONMENTAL QUALIFICATION, INTERCHANGEABILITY, DESIGN OR OPERATING PARAMETERS GENERATED DURING MANUFACTURE OF PROCESSING OF THIS ORDER. THIS REPORT SHALL INCLUDE TECHNICAL JUSTIFICATION FOR NONCONFORMANCE DISPOSITIONS. ALL DISPOSITIONS WHICH DO NOT RETURN AN ITEM TO THE CONDITIONS STATED IN AN APPROVED DRAWING OR SPECIFICATION SHALL BE APPROVED BY NEK PRIOR TO THE SHIPMENT OF THE AFFECTED ITEM.. G52 - CALIBRATION TEST RECORD. G53 - EQUIPMENT/ITEM QUALIFICATION TEST REPORT (EQTR). G80 - MATERIAL CERTIFICATE (CHEMICAL COMPOSITION AND MECHANICAL PROPERTIES). I13 - EMI/RFI QUALIFICATION THE SUPPLIER SHALL PROVIDE A CERTIFICATION SHOVING THE ITEM(S) HAS BEEN QUALIFIED IN ACCORDANCE WITH REG. GUIDE 1.180 REV.1 AND/OR EPRI TR-102323 REV.1. QUALIFICATION SHEET SHALL CLEARLY INDICATE EQUIPMENT ABILITY TO WITHSTAND ELECTROMAGNETIC INTERFERENCE, RADIO-FREQUENCY INTERFERENCE, AND POWER SURGES.. X100 - EQ EQUIPMENT FOLLOWING TECHNICAL AND QUALITY REQUIREMENTS SHALL BE MET: VENDOR SHALL CERTIFY THAT THE SUPPLIED EQUIPMENT IS ENVIRONMENTALLY QUALIFIED TO TEST REPORT D2013003 REV.C PERFORMED IN ACCORDANCE WITH IEEE STANDARD 323-1974 OR NEWER VERSION OF IEEE 323 STD. HOWEVER, IF THERE IS ANY DIFFERENCE (MATERIALS, DESIGN / CONSTRUCTION OR PERFORMANCE PARAMETERS) BETWEEN ORIGINALLY QUALIFIED EQUIPMENT AND SUBJECT SUPPLIED EQUIPMENT, THE DIFFERENCES SHOULD NOT DEGRADE ORIGINAL QUALIFICATION LEVEL IN ANY VIEWPOINT TO ACCOMPLISHING ITS SAFETY FUNCTION DURING AND SUBSEQUENT TO THE HARSH ENVIRONMENTS AT THE END OF QUALIFIED LIFE. ACCORDINGLY, SUPPORTING SIMILARITY ANALYSIS WITH REFERENCES SHALL BE PROVIDED TO CONFIRM ACCEPTABILITY OF DIFFERENCE. ALSO ORIGINALLY QUALIFIED EQUIPMENT DETERMINED QUALIFIED LIFE SHALL NOT BE DEGRADED. ANY CHANGE OF AGING SENSITIVE MATERIALS SHALL BE REPORTED IN SIMILARITY ANALYSIS TO DOCUMENT ACCEPTABILITY. IF MATERIAL CHANGE AFFECT QUALIFIED LIFE CHANGE, THAN SUFFICIENT DATA SHALL BE PROVIDED TO ENABLE NEW DETERMINATION OF QUALIFIED LIFE: - MATERIALS/PARTS IDENTIFICATION AND DESCRIPTION; - NEW AGING TEMPERATURE DEFINING ALSO OPERATING HEAT RISE (IF APPLICABLE) AND AGING TIME; - ACTIVATION ENERGY (EV) FOR APPLICABLE MATERIAL/PART....