## 1. SKLOP
zap.št. | št.opreme | lokacija | Opis opreme | Description of equipment | Enote | proizvajalec, tip, kataloška številka | cena/enoto EUR (brez DDV) | cena/enoto EUR (brez DDV)
serial number | no. of equipment | location |  |  | units | producer, type, catalogue number | price/unit EUR (without tax) | total price EUR (without tax)
|  |  | 1. SKLOP RASTLINJAKA | 1. SET OF GREENHOUSE
|  |  | Rastlinjak kot celota je razdelejen na dva sklopa izvedbe, pri čemer 1. sklop vsebuje izvedbo zunanjega ovoja rastlinjaka (konstrukcija iz aluminija z zasteklitevijo s pripadajočimi vrati in sistem senčenja), 2. sklop pa kompletno izvedbo notranjosti rastlinjaka vključno z regulacijo (predelne stene s pripadajočimi vrati, tlaki, električne, strojne in vodovodne inštalacije, senzorji in regulacija klimatskih pogojev ter mize) | The greenhouse as a whole is divided into two sets of construction, where the 1st set includes the construction of the outer casing of the greenhouse (aluminum construction with glazing with associated doors and shading system), and the 2nd set includes complete construction of the greenhouse interior including regulation (inner walls including doors, floors, electrical, mechanical and plumbing installations, sensors and regulation of climatic conditions and tables)
|  |  | Splošne zahteve za 1. sklop rastlinjaka: | General requiremens for the 1. set of greenhouse:
|  |  | 1. sklop rastlinjaka se izvede oz. montira na prej izvedeno nosilno jekleno konstrukcijo. Delavniška dokumentacija jeklene konstrukcije in izvedena jeklena konstrukcija bosta izvajalcu 1.etape rastlinjaka na voljo konec marca 2022. Jeklena konstrukcija bo izdelana iz cevnih profilov kvadratne in pravokotne oblike. Izvajelc bo lahko točne mere preveril na licu mesta. | The 1st set greenhouse is constructed or mounted on a previously executed roof slab and on a previously prepared load-bearing steel structure, which are not part of this bid. Construction plan documentation of steel structurwill be available at the end of March 2022 when the steel construction will be constructed. Steel construction will be made of square and rectangular pipe profiles. The contractor will be able to check the exact measurements on site.
|  |  | Izvajalec mora izdelati detajlni načrt izvedbe zasteklitve s senčili in ga uskladiti z odgovornim projektantom načrta arhitekture, pri čemer mora upoštevati: barva senčil in alu profilov je določena TIGER Drylec 29/60674 in je ni mogoče zamenjati, oblika senčil/brisolejev morajo biti deltoidnega preseka kot npr. Schuco TIP 168-730. Pri izdelavi načrta ni potrebno predvideti posebnega/ločenega odvajanja meteorne vode, le ta se odvaja na streho objekta kjer je že predvidem sistem za odvajnaje metorne vode. | The greenhouse supplier should provide detailed plan of glazing and shading that must be coordinated with the architectural project leader, taking into account: the color of the blinds and aluminum profiles is determined (TIGER Drylec 29/60674) and cannot be changed, the shape of the blinds / sunshades must be of deltoid cross-section such as e.g. Schuco TYPE 168-730. When making the plan, it is not necessary to envisage a special / separate drainage of meteor water, it is drained to the roof of the building where a system for drainage of meteor water is already planned.
|  |  | S ponudbo izvajelc/dobavitelj zagotavlja: > izdelavo delavniške dokumentacije zasteklitvenega sistema in sistema avtomatskega senčenja posamezne komore rastlinjaka (razen jeklene nosilne konstrukcije, ki je predmet osnovnega projekta stavbe, s čimer je definirana končna oblika celote), ki ga mora pred izvedbo potrditi naročnik in projektant, > senzoriko aktvnega sistema senčenja z vrtlivimi brisoleji po mednarodno veljavnih standardih, ki mora zagotavljati kompatibilnost z regulacijo sistema, ki bo izvedena v okviru 2. sklopa >vso potrebno dokumentacijo za izvedbo tehničnega pregleda v slovenskem jeziku > ostalo potrebno dokumentacijo za izvedbo in delovanje 1. sklopa rastlinjaka. | The offer must include the production of : > construction plan for the glazing system and for automatic shading system of each greenhouse chamber (except for the steel load-bearing structure, which is the subject of the basic design of the building, thus defining the final shape of the building), which must be approved by the client and architectural project leader > sensors of the active shading system with rotating sunshades according to internationally valid standards, which must ensure compatibility with the regulation of the system, which will be implemented within the 2nd set > all necessary documentation for the performance of the technical inspection in the Slovenian language > other necessary documentation for the implementation and operation of the 1st set of greenhouses.
|  |  | Ponudnik mora izbrati zasteklitev in senčila skladno z zahtevami, navedenimi v nadaljevanju. | The bidder must select glazing and blinds in accordance with the requirements listed below.
|  |  | Po končanju izvedbe 1. sklopa rastlinjaka mora dobavitelj opraviti zagon rastlinjaka, preizkusiti zrako- in vodotesnost rastlinjaka - skupaj s pooblaščenimi predstavniki naročnika - ter pripraviti vso potrebno dokumentacijo (kot npr.poročilo o opravljenih meritvah in delovanju rastlinjaka), potrebno za uspešno zvedbo tehničnega pregleda in pridobitev uporabnega dovoljenja. | After the completion of the 1st set of greenhouse construction, the supplier must start the greenhouse, test the airtightness and watertightness of the greenhouse - together with the authorized representatives of the client - and prepare all the necessary documentation (such as a report on the measurements and operation of the greenhouse) necessary for a successful technical inspection and obtaining a operating permit.
|  |  | Ponudba vključuje pripravo in predajo dokumentacije naročniku skladne s Pravilnikom o podrobnejši vsebini dokumentacije in obrazcih, povezanih z graditvijo objektov (Uradni list RS, št. 36/18, 51/18-popr. in 197/20). | The offer includes the preparation and submission of documentation to the client in accordance with the Rules on the detailed content of documentation and forms related to construction (Official Gazette of the Republic of Slovenia, No. 36/18, 51/18-.corr. and 197/20).
|  |  | Garancijska doba in pogoji garancije ter odzivni čas za servis je določen v splošnem delu razpisne dokumentacije. | The warranty period and warranty conditions, as well as the response time for service, are specified in the general part of the tender documentation.
|  |  | Ponudnik mora zagotoviti generalni pregled pred potekom garancijske dobe ter po končanem pregledu izvede meritve. V primeru odstopanja od specifikacij, odstope odpravi in preda ustrezno dokumentacijo. | The bidder shall provide a general inspection before the expiration of the warranty period and perform measurements after the completion of the inspection. In case of deviation from the specifications deviations are corrected and the documentation is given to the client.
1. |  |  | 1. SKLOP RASTLINJAKA | 1. SET OF GREENHOUSE | 1 |  |  | 0
|  |  | Dobava in montaža rastilnjaka zunanjih dimenzij 13,1 x 20,2 x 3,4 na spodnjem robu in 5,2 na zgornjem robu. Naklon strehe 7° (stopinj). Bruto tlorisna površina 201 m2. | Supply and installation of a greenhouse with external dimensions 13.1 x 20.2 x 3.4 m' at the bottom edge and 5.2 m' at the top edge. Roof pitch 7 ° (degrees).Gross floor area 201 m2.
|  |  | Konstrukcija zunanjega ovoja iz aluminija s izolacijskim termo členom, na rastru 1,4 m mora izpolnjevati naslednje karakteristike: | The construction of the outer casing made of aluminum with an insulating thermocouple, on a grid of 1.4 m, must meet the following characteristics:
|  |  | > širina profilov: do 50 mm | > profile width: up to 50 mm
|  |  | > globina profilov: skladno s statičnim izračunom (projektna hitrost 20 m/s) | > profile depth: according to static calculation (design wind velocity 20 m/s)
|  |  | > debelina zasteklitve: 40-56 mm (troslojna) | > glazing thickness: 40-56 mm (triple)
|  |  | > zračna prepustnost: AE 1200, EN 12152 | > air permeability: AE 1200, EN 12152
|  |  | > vodotesnost: po EN 12154 | > water resistance: according to EN 12154
|  |  | > odpornost na pritisk vetra: 2,4 kN/m2 po EN 13116 | > wind pressure resistance: 2.4 kN/m2 according to EN 13116
|  |  | > odpornost na udarec: I5/E5 po EN 14019 (varnostno steklo) | > impact resistance: I5/E5 according to EN 14019 (safety glass)
|  |  | > konstrukcijsko mora omogočati oz. mora biti kompatibilna z izbranimi vrtljivimi senčili oz. brisoleji | > structurally it must enable or it must be compatible with the selected movable (rotating blades) shading or brisse-soleils
|  |  | > barva profilov je določena TIGER Drylec 29/60674 in je ni mogoče spremeniti | > the color of the profiles is specified by TIGER Drylac 29/60674 and cannot be changed
|  |  | Troslojna zasteklitev, v ponujenem sestavu zunanjega ovoja, z varnsotno zasteklitvijo VSG, mora izpolnjevati naslednje pogoje: | In the offered composition of the outer casing, triple glazing with safety glazing VSG must meet the following conditions:
|  |  | > Ug ≤ 0,7 W/m2K (EN 673) | > Ug ≤ 0,7 W/m2K (EN 673)
|  |  | > g ≥ 60 % (EN 410) | > g ≥ 60 % (EN 410)
|  |  | > LT ≥ 70 % (EN 410) - Light Transmission | > LT ≥ 70 % (EN 410) - Light Transmission
|  |  | > CR ≥ 16 % (EN 410) - Colour Rendereing | > CR ≥ 16 % (EN 410) - Colour Rendereing
|  |  | > TEA ≤ 28% (Total Energy Absoption) | > TEA ≤ 28% (Total Energy Absoption)
|  |  | Površine posameznih delov zunanjega ovoja : | Area of individual parts of the outer casing:
|  |  | > streha: 207,5 m2 | > roof: 207,5 m2
|  |  | > južna fasada: 49,6 m2 | > south facade: 49,6 m2
|  |  | > severna fasada: 102,1 m2 | > north facade: 102,1 m2
|  |  | > vzhodna fasada: 66,0 m2 | > east facade: 66,0 m2
|  |  | > zahodna fasada: 66,0 m2 | > west facade: 66,0 m2
|  |  | > 1x izhodna steklena vrata v alu okvirju iz rastlinjaka na streho, svetlih dimenzij š/h = 95/210 cm | > 1x exit door: glass door in an aluminum frame from the greenhouse to the roof, clear opening w/h = 95/210 cm
|  |  | Senčenje z avtomatsko krmiljenimi senčili (brisoleji) iz aluminija širine 250-300 mm. Montaža na alumnijasto konstrukcijo rastlinjaka. Krmiljenje senčil mora biti sprogramirano tako, da bo mogoče neodvisno senčenje posamezne komore. Senčila za posamezno komoro morajo omogočati ločeno senčenje s stenskimi in strešnimi senčili. Komor v notranjosti rastlinjaka, ki niso predmet tega razpisa, je predvidenih 8. | Shading with automatically controlled blinds (brise soleils) made of aluminum blades, width 250-300 mm. Mounting on an aluminum construction of the greenhouse. The control of the blinds must be programmed in such a way that independent shading of each chamber is possible. Shades for each chamber must allow separate shading with wall and roof shades. There are 8 chambers inside the greenhouse, which are not the subject of this tender.
|  |  | > lamele na strehi širine 250-300 mm, površina 208 m2 | > roof blades, blade width 250-300 mm, area 208 m2
|  |  | > horizontalne lamele na južni fasadi širine 250-300 mm, površina 50 m2 | > horizontal blades on the south facade, blade width 250-300 mm, area 50 m2
|  |  | > horizontalne lamele na vzhodni fasadi širine 250-300 mm, površina 66 m2 | > horizontal blades on the east facade, blade width 250-300 mm, area 66 m2
|  |  | > horizontalne lamele za zahodni fasadu širine 250-300 mm, površina 66 m2 | > horizontal blades on the west facade, blade width 250-300 mm, area 66 m2
|  |  | > barva lamel je določenaTIGER Drylec 29/60674 in je ni mogoče spreminjati | > the color of the slats is determined by TIGER Drylac 29/60674 and cannot be changed
|  |  | > zasteklitev rastlinjaka se delno stika z fasadno zasteklitvijo osnovnega objekta. Izvajalec mora v delavniški dokumentacijo prikazati in z izvedbo zagotoviti vodotesnost navedenega stika v izmeri 2 x 2,3 m. Opisani stik je razviden iz priloge " prerez E-E , prikaz A11.18" | > the glazing of the greenhouse is partially in contact with the façade glazing of the basic building. The contractor must show in the construction plan documentation and ensure the watertightness of the said contact in the size of 2 x 2.3 m. The described contact can be seen in the appendix "section E-E, display A11.18"
|  |  | Skupaj brez DDV | TOTAL WITHOUT TAX |  |  |  | 0
|  |  | DDV | TAX |  |  |  | 0
|  |  | Skupaj z DDV | TOTAL WITH TAX |  |  |  | 0