## 2. SKLOP
zap.št. | št.opreme | lokacija | Opis opreme | Description of equipment | Enote | proizvajalec, tip, kataloška številka | cena/enoto EUR (brez DDV) | cena/enoto EUR (brez DDV)
serial number | no. of equipment | location |  |  | units | producer, type, catalogue number | price/unit EUR (without tax) | total price EUR (without tax)
|  |  | 2. SKLOP RASTLINJAKA | 2. SET OF GREENHOUSE
|  |  | Rastlinjak kot celota je razdelejen na dva sklopa izvedbe, pri čemer 1. sklop vsebuje izvedbo zunanjega ovoja rastlinjaka (konstrukcija iz aluminija z zasteklitevijo s pripadajočimi vrati in sistem senčenja), 2. sklop pa izvedbo notranjosti rastlinjaka vključno z regulacijo (predelne stene s pripadajočimi vrati, električne, strojne in vodovodne inštalacije, senzorji in regulacija klimatskih pogojev ter mize) | The greenhouse as a whole is divided into two sets of construction, where the 1st set includes the construction of the outer casing of the greenhouse (aluminum construction with glazing with associated doors and shading system), and the 2nd set includes complete construction of the greenhouse interior including regulation (inner walls including doors, electrical, mechanical and plumbing installations, sensors and regulation of climatic conditions and tables)
|  |  | Splošne zahteve za 2. sklop rastlinjaka: | General requiremens for the 2. set of greenhouse:
|  |  | 2. sklop rastlinjaka se izvede oz. montira na prej pripravljeno talno gradbeno osnovo in na izveden 1. sklop rastlinjaka. | 2. set of the greenhouse is constructed or mounted on a previously executed roof slab and a previously prepared 1. set of greenhouse.
|  |  | Dobavitelj rastlinjaka mora detajle izvedbe uskladiti z odgovornim projektantom načrta arhitekture pred pričetkom izdelave načrta rastlinjaka. | The greenhouse supplier must coordinate the construction details with the architectural project leader before starting the production of the greenhouse plan.
|  |  | Dobavitelj mora pri izdelavi rastlinjaka upoštevati: > največja dovoljena električna moč: 150 kW - 12,5 kW (za 5 rastnih komor reach-in, ki bodo nameščene v prostorih 02.07.02 in 02.07.10 znotraj rastlinjaka in niso predmet tega razpisa) = 137,5 kW (za 1. in 2. sklop rastlinjaka) > največja dovoljena moč naprav povezanih na diesel agregat oz. UPS: 150kW-DEA, 1kW-UPS > komunikacijski protokolih povezave na CNS sistem stavbe, Modubus RTU > največje dovoljeno število telekomunikacijskih priključkov (univerzalno ožičenje): 5 > razpoložljivi mediji (tehnični plini ipd.) > že predvidene lokacije in dimenzije talnih odtokov odpadne vode v komorah in predprostorih | The supplier must take into account when making the greenhouse: > maximum permissible electrical power: 150 kW - 12.5 kW (for 5 reach-in growth chambers, which will be installed in rooms 02.07.02 and 02.07.10 inside the greenhouse and are not the subject of this tender) = 137.5 kW (for the 1st and 2nd set of the greenhouse) > maximum permissible power of devices connected to the diesel generator or UPS: 150kW-DEA, 1kW-UPS > communication protocols connecting to the building's CNS system, Modubus RTU > maximum permitted number of telecommunication connections (universal wiring): 5 > available media (technical gases, etc.) > already planned locations and dimensions of floor effluents in chambers and anterooms
|  |  | Dobavitelj rastlinjaka mora v ponudbi za izdelavo rastlinjaka prikazati podatke potrebnih medijev za delovanje rastlinjaka , upoštevajoč predhodno navedene razpoložljive moči na objektu, kot so: > hladilna in ogrevna moč v kWh, > potrebna električna moč v kWh, > podatke o potrebnih močeh naprav povezanih na diesel agregat oz. UPS, > podatke o komunikacijskih protokolih povezave na CNS sistem stavbe, > podatke o številu telekomunikacijskih priključkov (univerzalno ožičenje) ter > ev. podatke o drugih medijih (tehnični plini ipd.) | In the greenhouse bid, the greenhouse supplier must specify the requirements for the necessary media for the operation of the greenhouse, taking into account previously stated available power capacities of the building, such as: > cooling and heating power in kWh, > required electrical power in kWh, > data on the required power of devices connected to the diesel generator or. UPS > data on communication protocols for connection to the building's BMS system, > data on the number of telecommunication connections (universal wiring) and > data on other media (technical gases, etc.) if needed
|  |  | Ponudba mora vključevati: > izdelavo delavniške dokumentacije (razen jeklene nosilne konstrukcije, aluminijaste konstrukcije, stekel in sistema senčanja, ki so predmet osnovnega projekta stavbe, s čimer je definirana končna oblika celote, oz. 1. sklopa rastlinjaka), ki ga mora pred izvedbo potrditi naročnik, > izvedbeni načrt strojnih instalacij (ogrevanje, hlajenje, prezračevanje z vlažanjem/sušenjem zraka, vodovod, odvajanje odpadne vode), > izvedbeni načrt električnih instalacij (splošna moč, razsvetljava), > centralni nadzorni sistem (CNS) samega rastilnjaka s povezavo na CNS stavbe, Vgrajen CNS sistem v rastlinjaku mora omogočat nastavljanje parametrov delovanja in nadzora delovanja sistemov na daljavo (online). > senzoriko klimatskih in svetlobnih pogojev v rastlinjaku (regulacija umetne in naravne svetlobe), ki mora biti kompatibilna s sistemom senčenja, ki bo izveden v okviru 1. sklopa rastlinjaka > ostalo potrebno dokumentacijo za izvedbo in delovanje rastlinjaka > dokumentacijo izvedenih del in vsa potrebna dokazila za izvedbio tehničnega pregleda in pridobitev uporabnega dovoljenja | The bid must include: > construction plan documentation (except for the load-bearing steel structure, aluminum structure with glazing and shading system, which are the subject of the basic design of the building, thus defining the final shape of the whole, or 1. set of greenhouse), which must be approved by the client before start of construction > construction plan of mechanical installations (heating, cooling, ventilation with humidification/air drying, plumbing and wastewater disposal) > construction plan of electrical installations (general power, lighting) > building management system (BMS) of the greenhouse with a connection to the building BMS. The greenhouse BMS must enable remote (online) setting of operating parameters and control of the operation of system. > sensors of climatic and light conditions in the greenhouse (regulation of artificial and natural light), which has to be compatible with the shading system, built in the 1. set of greenhouse construction > other necessary documentation for the implementation and operation of the greenhouse > documentation of all construction work and all evidences necessary for a successful technical inspection and obtaining an operating permit
|  |  | Ponudba mora obsegati dobavo in montažo notranjosti rastlinjaka vključno s predelnimi stenami s pripadajočimi vrati, z mizami po specifikaciji in vsemi komponentami strojnih, električnih in vodovodnih napeljav ter nadzornih sistemov vključno z napeljavami in končnimi distribucijskimi elementi (grelni in hladilni elementi, razsvetljava, cevi za zalivanje s šobami, senzorji ipd.). Ponudba mora obsegati merilnike temperature, vlage in svetlobe nad vsako mizo v vsaki komori. | The bid must include the supply and installation of the greenhouse interior, including inner walls with belonging doors, tables according to the specification; and all components of mechanical, electrical and plumbing installations; and control systems including installations and final distribution elements (heating and cooling elements, lighting, water hoses with nozzles, sensors, etc.). The offer must include temperature, humidity and light sensors above each table in each chamber.
|  |  | V tehnični etaži bodo priključki na dva tipa kanalizacij: - fekalno kanalizacijo in - onesnaženo kanalizacijo. Na fekalno kanalizacijo bosta priključena lijaka v 02.07.10 predprostoru in 02.07.02 sadilnici, ki nista predmet tega razpisa. Na onesnaženo kanalizacijo mora biti speljana vsa ostala odpadna voda iz notranjosti rastlinjaka. | The technical floor will have connections to two types of sewage systems: - faecal sewage system and - contaminated sewage system. To the faecal sewage system only the the two sink units in 02.07.10 anteroom and 02.07.10. planting room will be connected, which are not the subject of this tender All other wastewater from inside the greenhouse must be connected to contaminated sewage system.
|  |  | Ponudnik mora eventuealni kondenz in vso ostalo eventualno odpadno vodo od vseh strojnih strojnih naprav (npr. vlažilcev, razvlaževalcev, klim...) v vsaki komori speljati direktno na horizontalo onesnažene kanalizacije, ki se steka v jašek, kjer se vrši dekontaminacija onesnažene vode pred izlivom v javno kanalizacijo. | The bid must include the collection of all potential condensation water and any other potential waste water produced by any mechanical installation (e.g. humidifiers, dehumidifiers, fancoils...) in each chamber directly to the horizontal of the contaminated sewage system, which runs through a shaft where decontamination of polluted water is carried out before it outpours into the public sewage system.
|  |  | Korita miz v komorah naj nimajo odvoda odpadne vode. V rastlinjaku naj ne bo talnih sifonov. | Troughs of the tables in quarantine chambers should not have drainage of waste water. There should be no floor siphons in the greenhouse.
|  |  | Ponudnik mora z izborom strojnih (hlajenje, ogrevanje, prezračevanje) in električnih naprav (razsvetljava), senzorike in CNS sistema zagotoviti fizikalne pogoje z dovoljenimi odstopanji skladno s spodaj navedenimi zahtevami za vsako komoro posebej. | By selecting mechanical (cooling, heating, ventilation) and electrical devices (lighting), sensors and BMS, the bidder must provide physical conditions in the greenhouse with permitted deviations in accordance with the below requirements for each chamber separately.
|  |  | Vsaka komora v rastlinjaku mora pri delovanju omogočati in vsebovati: | In operation, each chamber in greenhouse must enable and contain:
|  |  | > nastavljanje klimatskih pogojev in svetlobnih pogojev po vnaprej določenem časovnem zaporedju (urniku), dan/noč ipd. ločeno po posameznih rastnih komorah rastlinjaka | > setting of climatic and lighting conditions according to a predetermined time sequence (schedule), day / night, etc., separately in each chamber of the greenhouse
|  |  | > programska oprema za nastavitev pogojev delovanja vsake komore | > software for settings of each camber conditions
|  |  | > online merjenje parametrov (temperartura, jakost svetlobe, relativne vlažnosti) | > online measurement of parameters (temperature, light intensity, relative humidity)
|  |  | > zbiranje podatkov v realnem času | > real-time data logging
|  |  | > web vmesnik | > web interface
|  |  | > LCD prikazovalnik na dotik (min 10'') | > LCD touch screen (min 10 '')
|  |  | > grafična predstavitev delovanja vsake komore (prikaz nastavljenih in trenutnih parametrov) | > graphical display of the operation of each chamber (display of set and current parameters)
|  |  | > prenos podatkov preko Etherneta ali USB vmesnika | > data transfer via Ethernet or USB interface
|  |  | > oddaljena kontrola delovanja preko LAN povezave | > remote operation control via LAN connection
|  |  | > diagnostični sistem za spremljanje in beleženje napak pri delovanju vsake komore | > diagnostic system for monitoring and recording of each chamber malfunctions
|  |  | Po končanju izvedbe rastlinjaka mora dobavitelj opraviti zagon rastlinjaka, preizkusiti delovanje ter nastaviti vse parametre delovanja rastlinjaka - vse skupaj s pooblaščenimi predstavniki naročnika - ter pripraviti poročilo o opravljenih meritvah in delovanju rastlinjaka. | After the completion of the greenhouse construction, the comissiong of the greenhouse, and testing of the operation and settings of all the parameters of the greenhouse should be performed - all together with the authorized representatives of the client - and prepare a report of the measurements and operation of the greenhouse.
|  |  | Ponudba mora vključevati pripravo in predajo dokumentacije naročniku skladno s Pravilnikom o podrobnejši vsebini dokumentacije in obrazcih, povezanih z graditvijo objektov (Uradni list RS, št. 36/18, 51/18-popr. in 197/20). | The bid should include the preparation and submission of documentation to the client in accordance with the Rules on the detailed content of documentation and forms related to construction (Official Gazette of the Republic of Slovenia, No. 36/18, 51/18-.corr. and 197/20).
|  |  | Garancijska doba in pogoji garancije ter odzivni čas za servis so določeni v splošnem delu razpisne dokumentacije. | The warranty period and warranty conditions, as well as the response time for service, are specified in the general conditions of the tender documentation.
|  |  | Dobavitelj ob dobavi opreme dostavi naročniku delovna navodila ter izvede usposabljanje vsaj 6 uporabnikov, čas trajanja usposabljanja je najmanj 3 dni in učenje na daljavo dodatnih 60 ur. | Upon delivery of the equipment, the supplier also delivers work instructions to the client and conducts training for at least 6 users for the duration at least 3 days and with the additional 60 hours on-line.
|  |  | Ponudnik mora zagotoviti generalni pregled pred potekom garancijske dobe ter po končanem pregledu izvesti meritve. V primeru odstopanja od specifikacij, odstope odpravi in preda ustrezno dokumentacijo. | The bidder should provide a general inspection before the expiration of the warranty period and perform measurements after the completion of the inspection. In case of deviation from the specifications deviations are corrected and the documentation is given to the client.
1. |  |  | Izdelava in oprema rastlinjaka | Construction and equipment of the greenhouse | 1 |  |  | 0
|  |  | Notranja izdelava in oprema rastilnjaka zunanjih dimenzij 13,1 m x 20,2 m x 3,4 m na spodnjem robu in 5,2 m na zgornjem robu. Naklon strehe 7° (stopinj). Bruto tlorisna površina 201 m2. Točne dimenzije ponudnik sam izmeri na lokaciji po izvedenem 1. sklopu rastlinjaka. | Interior construction and equipment of a greenhouse with external dimensions 13.1 m x 20.2 m x 3.4 m at the bottom edge and 5.2 m at the top edge. Roof pitch 7 ° (degrees). Gross floor area 201 m2. The bidder must measure the exact dimensions on the location after completition of the 1. set of the greenhouse.
|  |  | Rastlinjak je tlorisno deljen na 2 predprostora ter 8 karantenskih komor, površine (A) in volumna (V): | The floor plan of the greenhouse is divided into 2 anterooms and 8 quarantine chambers, of the following area (A) and volume (V):
|  |  | > predprostor komor 1; A = 7,2 m2; V = 35,0 m3 | > chamber anteroom 1; A = 7,2 m2; V = 35,0 m3
|  |  | > predprostor komor 2; A = 7,2 m2; V = 32,0 m3 | > chamber anteroom 2; A = 7,2 m2; V = 32,0 m3
|  |  | > karantenska komora 1; A = 43,9 m2; V = 193,7 m3 | > quarantine chamber 1; A = 43,9 m2; V = 193,7 m3
|  |  | > karantenska komora 2; A = 33,2 m2; ; V = 171,5 m3 | > quarantine chamber 2; A = 33,2 m2; ; V = 171,5 m3
|  |  | > karantenska komora 3; A = 10,8 m2; V = 56,0 m3 | > quarantine chamber 3; A = 10,8 m2; V = 56,0 m3
|  |  | > karantenska komora 4; A = 14,7 m2; V = 74,6 m3 | > quarantine chamber 4; A = 14,7 m2; V = 74,6 m3
|  |  | > karantenska komora 5; A = 18,5 m2; V = 91,8 m3 | > quarantine chamber 5; A = 18,5 m2; V = 91,8 m3
|  |  | > karantenska komora 6; A = 17,9 m2; V = 89,3 m3 | > quarantine chamber 6; A = 17,9 m2; V = 89,3 m3
|  |  | > karantenska komora 7; A = 10,5 m2; V = 43,3 m3 | > quarantine chamber7; A = 10,5 m2; V = 43,3 m3
|  |  | > karantenska komora 8; A = 10,4 m2; V = 43,2 m3 | > quarantine chamber 8; A = 10,4 m2; V = 43,2 m3
|  |  | skupna neto površina prostorov znotraj rastlinjaka: 174,3 m2 | total net area of rooms within the greenhouse: 174,3 m2
|  |  | Konstrukcija notranjih predelnih sten z vrati mora izpolnjevati naslednje karakteristike: | The construction of inner walls including doors must meet the following requirements:
|  |  | > pogledna širina AL profilacije 40 - 50 mm Ponudnik mora zagotoviti dovolj toge stene, ki bodo preprečevale tresenje sten pri uporabi vrat in zagotavljale ustrezno tesnost komor. Izvajalec mora za ta namen po potrebi predvideti dodatno podkonstrukcijo. Ustrezno togost je potrebno izkazati s statičnim izračunom, ki mora upoštevati horizontalno obremenitev 1kN. | > width of AL profile 40 - 50 mm The bidder must provide walls rigid enough to prevent any vibrations while using doors and ensure the appropriate sealing of the chambers. For this purpose, the bidder must provide additional subconstruction if needed. The appropriate rigidity of the walls must be proven with a static calculation, which must take into account the horizontal load 1kN.
|  |  | > globina do 60 mm | > depth up to 60 mm
|  |  | > zasteklitev z enojnim in dvoslojnim lepljenim varnostnim steklom VSG | > glazing with single and double-layered laminated safety glass VSG
|  |  | > višina sten se mora prilagajati naklonu strehe (višina 3,4 m do 5,1 m) | > the height of the walls must be adjusted to the slope of the roof (height 3.4 m to 5.1 m)
|  |  | > skupna površina notranjih steklenih sten 253,2 m2 | > total area of internal glass walls 253.2 m2
|  |  | > skupno število enokrilnih notranjih vrat svetle širine dim. 80/210 cm: 9 kosov (6 levih + 3 desnih vratnih kril) | > total number of single-leaf interior doors of clear width dim. 80/210 cm: 9 pieces (6 left + 3 right door wings)
|  |  | > skupno število dvokrilnih notranjih vrat svetle širine dim. 120/210 cm (primarno krilo 80 cm, sekundarno krilo 40 cm): 2 kos | > total number of double-leaf interior doors of clear width dim. 120/210 cm (primary wing 80 cm, secondary wing 40 cm): 2 pcs
|  |  | Mize | Tables
|  |  | Podnožja miz morajo biti izdelana iz vroče galvaniziranih jeklenih profilov, korita mize pa iz inox (nerjaveče jeklo) brez perforacij. Mize morajo biti visoke 72 cm ± 2 cm. | The bases of the tables must be made of hot-dip galvanized steel profiles and the troughs of the tables must be inox (stainless steel) without perforations. Tables should be 72 cm ± 2 cm high.
|  |  | Korita morajo biti izdelana iz kislinsko odpornega nerjavečega jekla v kvaliteti AISI 304 ali AISI 316L, finalna obdelava: fino brušeno; brez ostrih robov, vsi stiki varjeni v radiju 5 mm in fino prebrušeni. Robovi korit morajo biti višine 5 cm ± 2 cm od 3 cm do 8 cm. | Troughs must be made of acid-resistant stainless steel in AISI 304 or AISI 316L quality, final treatment: finely ground; no sharp edges, all joints welded within 5mm radius and finely ground. Sides of the troughs should be from 3 cm to 8 cm 5 cm ± 2 cm high.
|  |  | Korita morajo biti vodotesna. | The troughs must be waterproof.
|  |  | Za zalivanje mora biti v vsaki komori nameščena zalivalna cev z zalivalno šobo, ki omogoča doseg do vseh rastlin v komori. Zalivalne šobe morajo omogočati zalivanje brez škropljenja. | For watering, a watering hose with a watering nozzle must be installed in each chamber to allow access to all plants in the chamber. Watering nozzles should enable watering without spraying.
2. |  | 02.07.03. | Opis pogojev posameznih komor | Description of the conditions of individual chambers | 1 |  |  | 0
|  |  | Dimenzije posameznih komor je potrebno prilagoditi dejanskim izmeram lupine rastlinjaka (izdelane v okviru 1. sklopa rastlinjaka). Dimenzije miz je potrebno prilagoditi dejanskim izmeram posameznih komor tako, da je prostor maksimalno izkoriščen. | The dimensions of the individual chambers must be adjusted to the actual measurements of the outer casing of the greenhouse (constructed in the 1. set of the greenhouse). The dimensions of the tables must be adjusted to the actual measurments of the individual chambers in order of maximal usage of the available space.
2. |  | 02.07.03. | KARANTENSKA KOMORA 1 | QUARANTINE CHAMBER 1 | 1 |  |  | 0
|  |  | > površina 43,94 m2 | > area 43,94 m2
|  |  | > v komori 8x vtičnica 230 V, IP 44, enakomerno razporejene po komori | > in chamber 8x socket 230 V, IP 44, evenly distributed around the chamber
|  |  | > rastline iz semen ali tkivnih kultur | > plants from seeds and tissue cultures
|  |  | > število miz: 12, dimenzije miz: | > number of tables: 12, dimension of tables:
| L.02.07.03.M1 |  | 273,5 x 90 cm (dolžina x globina) | 273,5 x 90 cm (lenght x width)
| L.02.07.03.M2 |  | 273,5 x 90 cm (dolžina x globina) | 273,5 x 90 cm (lenght x width)
| L.02.07.03.M3 |  | 273,5 x 90 cm (dolžina x globina) | 273,5 x 90 cm (lenght x width)
| L.02.07.03.M4 |  | 173,5 x 90 cm (dolžina x globina) | 173,5 x 90 cm (lenght x width)
| L.02.07.03.M5 |  | 265,0 x 90 cm (dolžina x globina) | 265,0 x 90 cm (lenght x width)
| L.02.07.03.M6 |  | 258,0 x 90 cm (dolžina x globina) | 258,0 x 90 cm (lenght x width)
| L.02.07.03.M7 |  | 289,0 x 90 cm (dolžina x globina) | 289,0 x 90 cm (lenght x width)
| L.02.07.03.M8 |  | 226,5 x 90 cm (dolžina x globina) | 226,5 x 90 cm (lenght x width)
| L.02.07.03.M9 |  | 228,5 x 90 cm (dolžina x globina) | 228,5 x 90 cm (lenght x width)
| L.02.07.03.M10 |  | 228,5 x 90 cm (dolžina x globina) | 228,5 x 90 cm (lenght x width)
| L.02.07.03.M11 |  | 228,5 x 90 cm (dolžina x globina) | 228,5 x 90 cm (lenght x width)
| L.02.07.03.M12 |  | 228,5 x 90 cm (dolžina x globina) | 228,5 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 26,51 m2 | > total area of tables: 26,51 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: 18 - 30 °C | > temperature range: 18 - 30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability : ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50 - 75 % | > relative humidity: 50 - 75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber : ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
3. |  | 02.07.07. | KARANTENSKA KOMORA 2 | QUARANTINE CHAMBER 2 | 1 |  |  | 0
|  |  | > površina 33,16 m2 | > area 33,16 m2
|  |  | > v komori 6x vtičnica 230 V, IP 44, enakomerno razporejene po komori | > in chamber 6x socket 230 V, IP 44, evenly distributed around the chamber
|  |  | > rastline iz semen ali tkivnih kultur | > plants from seeds and tissue cultures
|  |  | > število miz: 9 | > number of tables: 9
| L.02.07.07.M1 |  | 307 x 90 cm (dolžina x globina) | 307 x 90 cm (lenght x width)
| L.02.07.07.M2 |  | 274 x 90 cm (dolžina x globina) | 274 x 90 cm (lenght x width)
| L.02.07.07.M3 |  | 275 x 90 cm (dolžina x globina) | 275 x 90 cm (lenght x width)
| L.02.07.07.M4 |  | 274 x 90 cm (dolžina x globina) | 274 x 90 cm (lenght x width)
| L.02.07.07.M5 |  | 307 x 90 cm (dolžina x globina) | 307 x 90 cm (lenght x width)
| L.02.07.07.M6 |  | 189 x 90 cm (dolžina x globina) | 189 x 90 cm (lenght x width)
| L.02.07.07.M7 |  | 189 x 90 cm (dolžina x globina) | 189 x 90 cm (lenght x width)
| L.02.07.07.M8 |  | 189 x 90 cm (dolžina x globina) | 189 x 90 cm (lenght x width)
| L.02.07.07.M9 |  | 189 x 90 cm (dolžina x globina) | 189 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 19,74 m2 | > total table area: 19,74 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: 18 - 30 °C | > temperature range: 18 - 30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50 - 75 % | > relative humidity: 50 - 75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber: ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
4. |  | 02.07.08. | KARANTENSKA KOMORA 3 | QUARANTINE CHAMBER 3 | 1 |  |  | 0
|  |  | > površina 10,83 m2 | > area 10,83 m2
|  |  | > v komori 2x vtičnica 230 V, IP 44 | > in chamber 2x socket 230 V, IP 44
|  |  | > rastline iz semen ali tkivnih kultur | > plants from seeds and tissue cultures
|  |  | > število miz: 3 | > number of tables: 3
| L.02.07.08.M1 |  | 159 x 90 cm (dolžina x globina) - POZOR: na načrtu je vrisana miza napačne dimenzije 307 x 90 cm (dolžina x globina) | 159 x 90 cm (lenght x width) - ATTENTION: on the plan this table is drawn in wrong dimensions 307 x 90 cm (lenght x width)
| L.02.07.08.M2 |  | 266 x 90 cm (dolžina x globina) | 266 x 90 cm (lenght x width)
| L.02.07.08.M3 |  | 307 x 90 cm (dolžina x globina) | 307 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 6,59 m2 | > total table area: 6,59 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: 18 - 30 °C | > temperature range: 18 - 30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50 - 75 % | > relative humidity: 50 - 75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber : ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
5. |  | 02.07.09. | KARANTENSKA KOMORA 4 | QUARANTINE CHAMBER 4 | 1 |  |  | 0
|  |  | > površina 14,66 m2 | > area 14,66 m2
|  |  | > v komori 2x vtičnica 230 V, IP 44 | > in chamber 2x socket 230 V, IP 44
|  |  | > rastline iz semen ali tkivnih kultur | > plants from seeds and tissue cultures
|  |  | > število miz: 3 | > number of tables: 3
| L.02.07.09.M1 |  | 448 x 90 cm (dolžina x globina) | 448 x 90 cm (lenght x width)
| L.02.07.09.M1 |  | 266,5 x 90 cm (dolžina x globina) | 266,5 x 90 cm (lenght x width)
| L.02.07.09.M1 |  | 307 x 90 cm (dolžina x globina) | 307 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 9,19 m2 | > total table area: 9,19 m2
|  |  | > zračni pritisk: podtlak 90 Pa | > air pressure: depression 90 Pa
|  |  | > temperaturni režim: 18 - 30 °C | > temperature range: 18 - 30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50 - 75 % | > relative humidity: 50 - 75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber: ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
6. |  | 02.07.11. | KARANTENSKA KOMORA 5 | QUARANTINE CHAMBER 5 | 1 |  |  | 0
|  |  | > površina 18,35 m2 | > area 18,35 m2
|  |  | > v komori 4x vtičnica 230 V, IP 44 | > in chamber 4x socket 230 V, IP 44
|  |  | > rastline od zunaj | > plants from outside
|  |  | > število miz: 4 | > number of tables: 4
| L.02.07.11.M1 |  | 587,5 x 90 cm (dolžina x globina) | 587,5 x 90 cm (lenght x width)
| L.02.07.11.M2 |  | 267 x 90 cm (dolžina x globina) | 267 x 90 cm (lenght x width)
| L.02.07.11.M3 |  | 443 x 90 cm (dolžina x globina) | 443 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 11,68 m2 | > total table area: 11,68 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: 18 - 30 °C | > temperature range: 18 - 30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50 - 75 % | > relative humidity: 50 - 75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber: ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
|  |  | Zagotoviti je potrebno zasteklitev proti karantenski komori 6, ki bo imela ustrezno toplotno prehodnost (Ug), ki bo manjša ali enaka 1,4 W/m2K | Glazing toward quarantine chamber 6 must provide appropriate thermal transmittance (Ug) that should be equal or lower to 1,4 W/m2K
7. |  | 02.07.12. | KARANTENSKA KOMORA 6 | QUARANTINE CHAMBER 6 | 1 |  |  | 0
|  |  | > površina 17,85 m2 | > area 17,85 m2
|  |  | > v komori 4x vtičnica 230 V, IP 44 | > in chamber 4x socket 230 V, IP 44
|  |  | > rastline od zunaj | > plants from outside
|  |  | > število miz: 3 | > number of tables: 3
| L.02.07.12.M1 |  | 587,5 x 90 cm (dolžina x globina) | 587,5 x 90 cm (lenght x width)
| L.02.07.12.M2 |  | 257 x 90 cm (dolžina x globina) | 257 x 90 cm (lenght x width)
| L.02.07.12.M3 |  | 440,5 x 90 cm (dolžina x globina) | 440,5 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 11,57 m2 | > total table area: 11,57 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: poletni režim 18 - 30 °C, zimski režim 4 - 24 °C | > temperature range: summer mode 18 - 30 °C, winter mode 4 - 24 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50 - 75 % | > relative humidity: 50 - 75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber: ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
|  |  | Zagotoviti je potrebno zasteklitev proti karantenski komori 5 in predprostoru komor 2 (vključno z vetrolovom), ki bo imela ustrezno toplotno prehodnost (Ug), ki bo manjša ali enaka 1,4 W/m2K | Glazing toward quarantine chamber 5 and the chamber anteroom 2 (including windshield) must provide appropriate thermal transmittance (Ug) that should be equal or lower to 1,4 W/m2K
8. |  | 02.07.13. | KARANTENSKA KOMORA 7 | QUARANTINE CHAMBER 7 | 1 |  |  | 0
|  |  | > površina 10,41 m2 | > area 10,41 m2
|  |  | > v komori 2x vtičnica 230 V, IP 44 | > in chamber 2x socket 230 V, IP 44
|  |  | > rastline od zunaj | > plants from outside
|  |  | > število miz: 3 | > number of tables: 3
| L.02.07.13.M1 |  | 306,5 x 90 cm (dolžina x globina) | 306,5 x 90 cm (lenght x width)
| L.02.07.13.M2 |  | 257 x 90 cm (dolžina x globina) | 257 x 90 cm (lenght x width)
| L.02.07.13.M3 |  | 158,5 x 90 cm (dolžina x globina) | 158,5 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 6,50 m2 | > total table area: 6,50 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: 18-30 °C | > temperature range: 18-30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore!) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50-75 % | > relative humidity: 50-75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber : ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
9. |  | 02.07.14. | KARANTENSKA KOMORA 8 | QUARANTINE CHAMBER 8 | 1 |  |  | 0
|  |  | > površina 10,45 m2 | > area 10,45 m2
|  |  | > v komori 1x vtičnica 230 V, IP 44 | > in chamber 1x socket 230 V, IP 44
|  |  | > ENTOMO | > ENTOMO
|  |  | > število miz: 3 | > number of tables: 3
| L.02.07.14.M1 |  | 306,5 x 90 cm (dolžina x globina) | 306,5 x 90 cm (lenght x width)
| L.02.07.14.M2 |  | 256 x 90 cm (dolžina x globina) | 256 x 90 cm (lenght x width)
| L.02.07.14.M3 |  | 158,5 x 90 cm (dolžina x globina) - POZOR: na načrtu je vrisana miza napačne dimenzije 306,5 x 90 cm (dolžina x globina) | 158,5 x 90 cm (lenght x width) - ATTENTION: on the plan this table is drawn in wrong dimensions 306,5 x 90 cm (lenght x width)
|  |  | > skupna površina miz: 6,49 m2 | > total table area: 6,49 m2
|  |  | > zračni pritisk: normalen | > air pressure: normal
|  |  | > temperaturni režim: 18-30 °C | > temperature range: 18-30 °C
|  |  | > temperaturna stabilnost: ±2 °C | > temperature stability: ±2 °C
|  |  | > temperaturna homogenost znotraj komore: ±2 °C (predvideti ustrezno število in lokacijo merilnih mest glede na velikost komore!) | > temperature spatial homogeneity within the chamber: ± 2 ° C (the bidder must predict the appropriate number and location of measuring points according to the size of the chamber)
|  |  | > vlažnost: 50-75 % | > relative humidity: 50-75 %
|  |  | > dovoljena odstopanja vlažnosti: ±5 % od nastavljene vrednosti | > humidity spatial homogeneity within the chamber : ± 5% of the set value
|  |  | > jakost osvetlitve (PPFD): najmanj 170 umol/m²s na razdalji 50 cm od vira svetlobe na vseh mestih površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 170 umol/m²s at a distance of 50 cm from the light at all positions on the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
|  |  | > homogenost jakosti osvetlitve znotraj komore: ±15 % na površini mize v temi ob prižganih lučeh | > illumination spatial homogeneity within the chamber: ±15% on the surface of the table (lights on, dark outside)
|  |  | > valovna dolžine osvetlitve (K): LED osvetlitev, hladno bela svetloba celotnega spektra (čim bolj podobna sončni svetlobimed 5100 K in 5800 K) 5700 K + dolgovalovna rdeča 735 nm. | > illumination wavelength (K): LED illumination, cool full spectrum white lights (as similar to the sun light as possiblebetween 5100 K and 5800 K) 5700 K + far-red 735 nm.
|  |  | > Luči morajo biti nastavljive po višini. | > Lights must be height adjustable.
|  |  | Skupaj brez DDV | TOTAL WITHOUT TAX |  |  |  | 0
|  |  | DDV | TAX
|  |  | Skupaj z DDV | TOTAL WITH TAX