Project name: Upgrading national research infrastructures– RIUM

Declaration of Compliance with the Contracting Authority’s Minimum Technical Requirements and Specifications of the Offered Equipment

Name of the tenderer:

Address of the tenderer:

Subject of the public procurement: Procurement of a modular clean room

Designation of the public procurement: 302/17 – RIUM75-P10-FERI 03.8/2022

| Is the tenderer also the manufacturer of the offered equipment? | YES ☐ | NO ☐* |
| --- | --- | --- |
| *If the answer is NO, enter the equipment manufacturer's name and address: |  |  |

INSTRUCTIONS:

- This Attachment No. 2 has to be completed and signed. The tenderer has to specify the actual technical specifications of the offered equipment in compliance with all the requirements.

- The tenderer uploads this Attachment No. 2 in Word and PDF format (including the enclosed means of proof for meeting all technical requirements) to the e-JN information system, section “Other attachments”.

We declare that the offered equipment fully complies with the minimum technical requirements of the Contracting Authority for the subject-matter of the public procurement entitled “Procurement of a modular clean room”, and that we are prepared to perform the public contract according to the following specification:

| EQUIPMENT |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | REQUIREMENTS | OFFERED |  |  |  |  | DATASHEET |
| 1 | Modular clean room dimensions: |  |  |  |  |  |  |  |
|  | - Inner dimensions: length minimal 5000 mm; width minimal 4000 mm; height minimal 2500 mm | Length: _______________ mm |  |  |  |  |  |
|  |  | Width: _______________ mm |  |  |  |  |  |
|  |  | Height: _______________ mm |  |  |  |  |  |
|  | - Outer dimensions: height maximum 3000 mm | Height: _______________ mm |  |  |  |  |  |
|  | Partition walls of the modular clean room: |  |  |  |  |  |  |  |
|  | - Material: Aluminium (ALU) | - YES |  | - NO |  |  |  |
|  | - Final layer: powder coated | - YES |  | - NO |  |  |  |
|  | - Thickness: minimal 50 mm | Thickness: _______________ mm |  |  |  |  |  |
|  | - Glazing of minimal two (2) partition walls. | - YES |  |  | - NO |  |  |
|  | - Glazing dimensions: height minimal 1200 mm; width minimal 1200 mm | Height: _______________ mm |  |  |  |  |  |
|  |  | Width: _______________ mm |  |  |  |  |  |
|  | - Glazed with dual Thermopan glass. | - YES |  |  | - NO |  |  |
|  | - Final layer color: RAL 9001 | - YES |  |  | - NO |  |  |
|  | Modular clean room door: |  |  |  |  |  |  |  |
|  | - Door leaf width: minimal 1000 mm | Width: _______________ mm |  |  |  |  |  |
|  | - Door leaf height: minimal 2000 mm | Height: _______________ mm |  |  |  |  |  |
|  | - Door leaf thickness: minimal 50 mm | Thickness: _______________ mm |  |  |  |  |  |
|  | - Glazed door leaf with the following glass dimensions: height minimal: 700 mm; width minimal 500 mm. | Height: _______________ mm |  |  |  |  |  |
|  |  | Width: _______________ mm |  |  |  |  |  |
|  | - Glazed with dual Thermopan glass. | - YES |  | - NO |  |  |  |
|  | - Door leaf with built in floor seal. | - YES |  | - NO |  |  |  |
|  | - Magnet door closing without additional rubber seals. | - YES |  | - NO |  |  |  |
|  | - Possibility of quick assembly and disassembly of the door leaf. | - YES |  | - NO |  |  |  |
|  | - Enabled door leaf opening to 180 degrees. | - YES |  | - NO |  |  |  |
|  | - Final layer color: RAL 9001 | - YES |  | - NO |  |  |  |
|  | - Door frame: anodized | - YES |  | - NO |  |  |  |
|  | Filtering system: |  |  |  |  |  |  |  |
|  | - Minimal ISO 7 class (according to the 14644-1:2015 standard) filtering system. | - YES |  | - NO |  |  |  |
|  | - Manual or automatic controlling venting system. | - Manual |  | - Automatic |  |  |  |
|  | - Fan filtering unit (FFU) count: minimal two (2) sets | - YES |  | - NO |  |  |  |
|  | - Fan filtering unit (FFU) noise: maximum 50 dB | FFU noise: __________________ dB |  |  |  |  |  |
|  | - Filters: minimal 14 HEPA and G4 pre-filter | - YES |  | - NO |  |  |  |
|  | - Air overpressure supply device in a clean room. | - YES |  |  | - NO |  |  |
|  | Flooring: |  |  |  |  |  |  |  |
|  | - Antistatic epoxy floor. | - YES |  |  | - NO |  |  |
|  | - Antistatic design with adequate static electricity discharge design electricity by earthing. | - YES |  |  | - NO |  |  |
|  | Electrical installations, lighting and computer network: |  |  |  |  |  |  |  |
|  | - Parapet trunk with minimal six (6) sockets | Number of sockets: __________________ |  |  |  |  |  |
|  |  | Minimal two (2) sockets must be compatible with high power devices, minimal 5000 W | - YES |  |  | - NO |  |
|  | - Minimal two (2) ethernet sockets | Number of ethernet sockets: ________________ |  |  |  |  |  |
|  | - Ceiling lightning with LED light, lightning minimal 500 Lux per light | Lightning of a dedicated light: _____________________ lux |  |  |  |  |  |

| Place and date: | Stamp: | Authorized signature: |
| --- | --- | --- |

The operation is co-financed by the Republic of Slovenia, Ministry of Education, Science and Sport and the European Union from the European Regional Development Fund. The operation is carried out under priority axis 1 of the Operational Program for Implementation of the European Cohesion Policy 2014–2020: “International competitiveness of research, innovation and technological development, in line with smart specialization for increased competitiveness and greening of the economy”, priority investment 1.1 “Strengthening R&D infrastructure and capacity to develop excellence in this and the promotion of competent centers, especially those of European importance”, specific objective 1.1.1 “Efficient use of research infrastructure and development of knowledge/competences for better national and international cooperation in the knowledge triangle”.

The tenderer has to specify the actual technical specifications of the offered equipment in compliance with all the requirements.

The tenderer has to indicate the name of the accompanying equipment manufacturer’s catalogue or brochure and number of the page containing the relevant technical specifications. In exceptional cases, the tenderer may also provide a link to the website of the equipment manufacturer which includes an indication of the relevant technical specifications. Where a link to the online document is provided, the tenderer has to provide the number of the page containing the relevant technical specifications.