## List1
NOTE: | For completion of the table, see Schedule of Technical Data - Instructions
Item | Description of equipment to be supplied | Unit | Design/required data | Tenderer’s data
1.0 | Power unit basic data
1.0.1 | * Rated flow rate | m3/s | 5 * |  | YES
1.0.2 | Maximum operating flow Minimum operating flow | m3/s | ≤ 7 ≥ 0.5 |  | NO
1.0.3 | * Available site height | m | 6.74 *
1.0.4 | Unit efficiency including inverter | %
1.1 | Archimedes screw turbine
1.1.1 | Archimedes screw material |  | Steel min. S355 (St 37-2) or higher quality
1.1.2 | Archimedes screw casing (steel cladding with anchors for anchoring in concrete) |  | Steel min. S235 or higher quality, min. thickness 4 mm
1.1.3 | Power | kW | ≥ 235
1.1.4 | Number of revolutions | 1/min | 20 to 25
1.1.5 | Over speed in the event of a mains failure without braking | 1/min | ≤ 80
1.1.6 | Min. hours of operation | h | ≥ 300,000
1.1.7 | Upper bearing Min. hours of operation | h | ≥ 100,000
1.1.8 | Lower bearing Min. hours of operation | h | ≥ 100,000
1.1.9 | Total weight of power unit | t | 40 to 42
1.1.10 | Outer diameter of the runner | m | 3.4 to 3.8
1.1.11 | Total actual length of the power unit (turbine, bearings, clutch(s), multiplier, generator and brake) | m | 18.15 (± 0.15)
1.1.12 | Turbine runner length | m | 13 to 14
1.1.13 | Inclination angle of the power unit |  | 28° to 32°
1.1.14 | Runner/cladding gap | mm | ≤ 10
1.1.15 | Noise level at 1 m | dB | ≤ 72
1.1.16 | Anti-corrosion protection
1.1.16.1 | All external surfaces in contact with water
1.1.16.1.2 | Surface preparation |  | YES/NO
| Degreasing with organic solvent |  | YES/NO
| * Sandblasting in Sa 2 ½ quality according to ISO 8501-1/1988 |  | Sa 2 ½ according to ISO 8501-1/1988 *
1.1.16.1.3 | Base coating
| Two-component primer based on an epoxy binder with a high zinc powder content (such as SIKACOR ZINC R) or equivalent | μm | ≥ 50
1.1.16.1.4 | Intermediate coating
| Two-component epoxy resin-based coating (such as SIKA POKSICOLOR SW) RAL 7032 or equivalent | μm | 2 x ≥ 180
1.1.16.1.5 | Final coating
| Two-component coating based on epoxy resins or polyurethane (such as SIKACOR EG5) RAL7042 or equivalent | μm | ≥ 40
1.1.16.2 | All internal surfaces not in contact with water
1.1.16.2.1 | Surface preparation |  | YES/NO
| Degreasing with organic solvent |  | YES/NO
| * Sandblasting in Sa 2 ½ quality according to ISO 8501-1/1988 |  | Sa 2 ½ according to ISO 8501-1/1988 *
1.1.16.2.2 | Base coating
| Two-component primer based on an epoxy binder with a high zinc powder content (such as SIKACOR ZINC R) or equivalent | μm | ≥ 50
1.1.16.2.3 | Intermediate coating
| Two-component epoxy resin-based coating (such as SIKA POKSICOLOR SW) RAL 7032 or equivalent | μm | ≥ 180
1.2 | Power transmission
1.2.1 | Clutch
1.2.1.1 | Manufacturer |  | Siemens-Flender or equivalent
1.2.1.2 | Type of clutch |  | Elastic toothed three-piece clutch or equivalent
1.2.1.3 | Rated torque | kNm | from 135 to 165
1.2.1.4 | Safety factor |  | ≥ 1,3
1.2.2 | Reducer/multiplier
1.2.2.1 | Manufacturer |  | Siemens or equivalent
1.2.2.2 | Type |  | Gear drive or equivalent
1.2.2.3 | Min. hours of operation | h | ≥ 100,000
1.2.2.4 | Rated torque | kNm | 230 to 250
1.2.2.5 | Gearbox efficiency | %
1.2.2.6 | Safety factor |  | ≥ 2.0
1.2.2.7 | Weight | kg | 4900 to 5100
1.2.3 | Secondary clutch
1.2.1.1 | Manufacturer |  | Siemens or equivalent
1.2.1.2 | Typo of clutch |  | Elastic toothed two-piece clutch or equivalent
1.2.1.3 | Rated torque | kNm | 7.0 to 8.4
1.2.1.4 | Safety factor |  | ≥ 2.6
1.3 | Generator
1.3.1 | Manufacturer |  | Siemens or equivalent
1.3.2 | Nominal power | kW | ≥ 250
1.3.3 | Rated rotational speed | 1/min | 900 to 1100
1.3.4 | * Voltage | V | 400 *
1.3.5 | * Frequency | Hz | 50 *
1.3.6 | * Protection type |  | IP 55 *
1.3.7 | * Winding protection |  | PT 100 *
1.3.8 | * Winding efficiency class |  | IE3 *
1.3.9 | Generator rated current | A
1.3.10 | Generator efficiency | %
1.3.11 | Winding insulation level |  | F or higher
1.4 | Safety brake
1.4.1 | Manufacturer |  | Siemens or equivalent
1.4.2 | Type |  | Brake with a hydraulic thruster and a separate hydraulic unit or equivalent
1.4.3 | Rated torque | kNm. | 8.0 to 8.5
1.4.4 | Safety factor |  | ≥ 2
1.5 | Electrical equipment
1.5.1 | * +CNA01 power unit control enclosure |  | In accordance with section 6.6 of the Technical description including technical data *
1.5.2 | * Water level measurement equipment |  | In accordance with section 6.7 of the Technical description including technical data *
1.5.3 | * LV enclosure for generator circuit breaker and grid disconnection point (+BAA02) |  | In accordance with section 6.5 of the Technical description including technical data *
1.5.4 | * Cable connections |  | In accordance with section 6.8 of the Technical description including technical data *
1.6 | Frequency converter (+BAA01)
1.6.1 | Manufacturer |  | Siemens, ABB or equivalent
1.6.2 | Type
1.6.3 | * Mains voltage | V | 3x380/400/415 *
1.6.4 | Frequency | Hz | 48 ... 63
1.6.5 | Rated power at ambient temp. 40° | kV | ≥ generator power
1.6.6 | Rated current at ambient temp. 40° | A | ≥ generator rated current
1.6.7 | * Built-in electromagnetic interference (EMI) filter according to EN 61800-3 |  | YES *
1.7 | Safety gate
1.7.1 | Type |  | Sliding gate in side guides or equivalent
1.7.2 | * Dimensions of the gate | mm | 4830 /2460 *
1.7.3 | * Steel structure |  | S355J2+N *
1.7.4 | * Drive |  | Double-sided hydraulic drive with gear transmission *
1.7.5 | * Hydraulic oil |  | Biodegradable hydraulic oil *
1.7.6 | * Sealing |  | Three-way sealing *
1.7.7 | * Maximum closing time | s | 10 *
1.7.8 | Anti-corrosion protection
1.7.8.1 | Sandblasting, Sa 2 ½ according to ISO 8501-1/1988 |  | Sa 2 ½ according to ISO 8501-1/1988 *
1.7.8.2 | Primer: Zn - Epoxy | μm | ≥ 50
1.7.8.3 | Intermediate coatings: Epoxy coating with glass flakes, coating 2x | μm | 2 x ≥ 200
1.7.8.4 | Finishing coating: Tectyl 506 or Anticorit BW 366 or equivalent | μm | ≥ 40
1.8 | Hydraulic unit
| Hydraulic unit |  | Hydraulic gear pump or equivalent
| Drive |  | AC electric motor or equivalent
| Working pressure | bar | ≤ 130
| Oil tank volume | l | ≤ 25
| Biodegradable hydraulic oil |  | For example Panolin HLP Synth 32 or equivalent