Pesnica SHPP

TENDER DOCUMENTS

LOT TG

VOLUME 3

PART I: Technical description including technical data

September 2022

CONTENTS

1.	General	4

1.1	Basic information about the plant	4

1.2	Location of the Pesnica SHPP	5

1.3	Design of the Pesnica SHPP	6

2.	Description of THE existing situation and condition	6

2.1	Hydrological conditions	6

3.	design fundamentals	8

4.	DESCRIPTION OF THE PLANT DESIGN AND SOLUTION	10

4.1	DESCRIPTION OF SHPP FACILITIES	12

5.	General requirements for electrical equipment	17

5.1	General	17

5.2	Standard voltages	17

5.3	Colour coding	18

5.4	Design of the devices	18

5.5	Electric motors	18

5.6	Electrical enclosures	19

5.7	EMC requirements	20

5.8	Terminal blocks	21

5.9	Wiring	21

5.10	Labelling of equipment and conductors	22

5.11	Cables	22

5.12	Earthing	22

5.13	Equipment parameterisation	23

5.14	Equipment for control and supervision	23

6.	Special requirements for electrical equipment	24

6.1	MV switchgear equipment	25

6.2	20/0.4 kV transformer	25

6.3	Electrical generator of the unit	26

6.4	Frequency converter enclosure +BAA01	27

6.5	LV enclosure for generator circuit breaker and grid disconnection point +BAA02	28

6.6	Unit control equipment and communication equipment +CNA01	30

6.7	Measuring water levels	31

6.8	Cable connections	31

7.	Execution of works	32

7.1	Time constraint for works	32

7.2	Contractors and equipment suppliers involved in construction	32

8.	Technical data	33

8.1	Power unit	33

9.	Services covered by this invitation to tender	38

9.1	Supply of equipment	38

9.2	Installation, testing, commissioning and training of the Client's personnel	38

9.3	Documentation	38

9.4	Spare Parts	42

9.5	Warranty maintenance	42

9.6	Commercial terms for the supply and installation of equipment	42

9.7	Start-up	43

General

Basic information about the plant

The present design documentation has been prepared for the Client DEM on the basis of Terms of Reference from 2021. Previously, documentation was prepared for a flood relief channel at the site of the Pesnica River for this location, but the terrain and water use conditions have changed to such an extent that new documentation is needed.

Some basic information about the location:

Pesnica River positioning at the membrane site

- km 3 + 107

Mean annual flow of the Pesnica River at the membrane site

- sQs = 5.19 m3/s

100-year water flow rate of the Pesnica River at the membrane site

- Q100Pesnica = 170 m3/s

Size of the Pesnica river basin up to the location of the membrane

- F = 479.76 km2

River positioning of the Pesnica flood relief channel at the location of the overflow into the discharge channel of the SD2 HPP

- km 10 + 000 of the discharge channel of the SD2 HPP

Reference flow through the Pesnica flood relief channel

- Q100 = 140 m3/s

Head water elevation at the Pesnica intake structure

- Hzg = 199.80 m

The more significant tail water elevations in the discharge channel during the operation of the Formin HPP in combination with the flow rate in the Drava riverbed and the Pesnica flood relief channel at the normal damming elevation of the Varaždin HPP:

- at a flow rate of 0 m3/s and in the Drava riverbed 10 m3/s	Hsp = 191.00 m

- at a flow rate of 550 m3/s and in the Drava riverbed 10 m3/s	Hsp = 192.36 m

- at a flow rate of 550 m3/s, in the Drava River 2990 m3/s and in the flood relief channel 140 m3/s   Hsp = 194.71 m

Installed/maximum (short-term) turbine flow

- Qi = 5 m3/s / Qmax = 7 m3/s

Location of the Pesnica SHPP

Pesnica SHPP is located on the left bank of the Formin HPP discharge channel, next to the Pesnica River flood relief channel at the river positioning of the Formin HPP discharge channel at km 10 + 000.

Figure 1: Illustration of the area and facilities of the planned Pesnica SHPP

Design of the Pesnica SHPP

The Pesnica SHPP is planned on the left side of the Pesnica River flood relief channel, on the high-water embankment of the Formin HPP discharge channel. The solution is designed in such a way that the run-of-river SHPP would take water from the Pesnica River and discharge it into the Formin HPP discharge channel. Solutions are designed in a way that they make the most of the existing infrastructure.

Pesnica SHPP is composed of the following key facilities:

- high-water membrane in the Pesnica riverbed with hydro-mechanical equipment and a passage for aquatic organisms,

- a lateral intake structure with trash rack,

- a 27 m long and 0.5 m high inflatable rubber dam in the flood relief channel’s bed,

- supply channel with a floor outlet and threshold,

- intake to the channel of the power house with an Archimedes screw.

The investor will only exploit the water of the Pesnica River when the flow rates in the Pesnica River riverbed below the location of the high-water membrane are guaranteed, as agreed in working meetings with the Institute of the Republic of Slovenia for Nature Conservation:

  - dry season (Jan, Feb, Aug, Sep, Oct, Nov, Dec) – 0.93 m3/s

  - wet season (March) – 1.19 m3/s

  - April and May – 4,5 m3/s

  - June and July – entire natural inflow (up to flow rates of 10 m3/s).

Description of THE existing situation and condition

The description of the existing situation and condition contains descriptions of:

- the hydrological situation,

- geological and geomechanical conditions,

- ecological conditions,

- descriptions of existing infrastructure facilities:

  - high-water membrane,

  - relief spillway,

  - embankment of the Formin HPP discharge channel,

  - access routes,

  - public utility infrastructure.

Hydrological conditions

There are three bodies of water in the area:

- the Pesnica River,

- the Zvirenčina Stream and

- the discharge power canal of the Formin HPP.

It should be noted that the Pesnica River and the Zvirenčina Stream are natural watercourses, while the Formin HPP discharge channel is a power canal with fluctuating levels as a result of the operation of the Formin HPP and the lower dam structure before Lake Ormož.

Pesnica River and Qes

Daily hydrological data for the water metering station Zamušani I for the period 1961-2016 were obtained. The hydrological data from the ARSO hydrological archive and reduced by the ecologically acceptable flow rate given in the water permit (in preparation):

  - dry season (Jan, Feb, Aug, Sep, Oct, Nov, Dec) – 0.93 m3/s

  - wet season (March) – 1.19 m3/s

  - April and May – 4,5 m3/s

  - June and July – entire natural inflow (up to flow rates of 10 m3/s).

The available flow rate duration curve is given in the table below, which has been further verified in a report by DEM d.o.o. "Report on tests and measurements carried out for the Pesnica facility", dated 13.12.2017. Daily flow rates for the period 1946-2016 are given in Annex 1 of this report.

Table 1: Duration curve of available flow rates for exploitation of the energy hydropotential (based on the period 1946-2016).

| months | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Flow rate | 132 | 11.57 | 5.92 | 3.47 | 2.12 | 1.30 | 0.71 | 0.25 | 0 | 0 | 0 | 0 | 0 |

Table 2: Duration curve of available flow rates for exploitation of the energy hydropotential (based on the period 2000-2016).

| months | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Flow rate | 96 | 10.07 | 5 | 2.81 | 1.74 | 1.06 | 0.58 | 0.15 | 0 | 0 | 0 | 0 | 0 |

Discharge power canal of the Formin HPP, Drava River at the Borl water metering station and the Pesnica River flood relief channel

The water level in the power canal of the Formin HPP depends on:

- the operating mode of the Formin HPP,

- flow rate in the bed of the Drava River,

- flow rate in the Pesnica River,

- the elevation of the water surface of Lake Ormož.

Return periods at the Borl water metering station and high-water conditions along the Drava River

Drava River flow rates at the Borl water metering station, taken from VGB design, plan number 3411/12, March 2013.

sQs = 309 m3/s 	(before the construction of Formin HPP)

| Return period | Q2 | Q5 | Q10 | Q20 | Q30 | Q50 | Q100 | Q300 | Q500 | Q1000 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Q (m3/s) | 1251 | 1709 | 2027 | 2342 | 2530 | 2769 | 3103 | 3662 | 3934 | 4320 |

Table 3: Return periods of high-water levels of the Drava River (Borl water metering station)

Formin HPP discharge channel

The 10 km long Formin HPP discharge channel runs from the power house of the Formin HPP to the outflow into the Drava River at Ormož. The section under consideration is located 1.4 km downstream from the Formin HPP power house building. The discharge channel is embedded in the marlstone base, on the left side as an embankment, and on the right side it continues into a higher gravel terrace.

The sealing of the discharge channel is provided by two sealing curtains running parallel to the channel. They are embedded vertically in the ground and extend from the marlstone base to the ground surface along the discharge channel.

The embankment crest along the discharge channel is equipped with a road for the operators of the Formin HPP. In the discharge channel, there are two access berms on the bank at an elevation of approx. 195.00 m (right bank) and 195.40 m (left bank in the area of the flood relief channel’s bed), which are accessible from the crown of the discharge channel embankments by means of access ramps.

design fundamentals

For designing purposes, the designer used the existing design documentation:

- Pesnica SHPP flood relief channel IDP, HSE Invest

- Documentation for the initiative for the granting of concession for Pesnica SHPP, VGB d.o.o., no. 3391/12, July 2012

- Pesnica flood relief channel at km 10+000 in O.K. SD 2 - As-built documents, project number VGB 940/4-83, folder I, February 1983

- Pesnica flood relief channel at km 10+000 in O.K. SD 2 - As-built documents, folder II and III, project number VGB d.o.o. 940/4-83, February 1983

- Partial water use permit no: 35523-298/2013-13, dated 22.10.2013

- Surveying image of the ground condition dated 12.11.2013

- Expert bases for the planning of the SHPP flood relief channel on the Pesnica River. Study 3519/14, VGB d.d., Maribor, July 2014

- Splitting of the flow rate of the Pesnica River at the Formin relief structure, Study no. 3519/14D, Maribor, November 2014

- Obtained design conditions and solutions aligned with the design conditions consent

  - Fisheries Research Institute of Slovenia

  - Nature Conservation Consent

  - Water consent, Slovenian Water Agency, Maribor branch

  - Design conditions Elektro Maribor d.d.

  - Municipalities of Gorišnica and Ormož

- Report No. 4749 on the inspection of the structural elements of the discharge channel of the Formin HPP Apros dated 17.7.2021

- Geological report: "Geomechanical investigations on the Pesnica flood relief channel", numbered: 012-GP/2021-TV, produced by RGP d.o.o. in September 2021.

- Analysis of the hydraulic conditions of the Formin HPP supply/discharge channel with the Ptuj Lake reservoir, report number 1042, produced by Hidroinštitut (Institute for Hydraulic Research) in March 2018

- Preliminary tender for turbine equipment and generator

DESCRIPTION OF THE PLANT DESIGN AND SOLUTION

The subject of the project is the construction of a SHPP on the existing water infrastructure, the flood relief channel of the Pesnica River. The subject is a small hydroelectric power plant with irreversible water withdrawal from the Pesnica River relief channel, and its diversion to the Formin HPP discharge channel. The power plant consists of the following key facilities with the auxiliary mechanical, hydromechanical and electrical equipment and installations:

- existing high-water membrane (RC wall with an opening) on the Pesnica River equipped with a flow control gate with an opening in the gate for the passage of aquatic organisms,

- intake structure with trash rack,

- supply channel from the intake structure to the power house channel with a floor threshold,

- power house channel with an integrated Archimedes screw,

- outlet into the Formin HPP discharge channel,

- inflatable rubber dam, impoundment height: 0.5 m, length: 27 m, built into the flood relief channel,

- connection to utility and public infrastructure lines; and

- access roads to and around the transport platform.

Additional major interventions during construction are foreseen to meet the needs of the construction pits.

| Figure 2: Ground plan (top) and cross-section (bottom) of the Pesnica SHPP |  |
| --- | --- |

The following is set out hereinafter:

- descriptions of key facilities and equipment with associated calculations,

- a proposal for the layout of facilities and equipment,

- a description of the necessary measures to be taken during construction,

- calculation of produced energy.

DESCRIPTION OF SHPP FACILITIES

Intake structure

The intake system consists of the following facilities:

- Pesnica River riverbed and flood relief channel,

- intake,

- bag-shaped rubber dam, approx. 27.0 m long, 0.5 m high, on a new concrete foundation,

- high-water membrane with regulated discharge to ensure Qes and passage of aquatic organisms.

Pesnica River riverbed and flood relief channel

The Pesnica River has a lowland character; a low head of between 1-2% and low velocities, depending on the hydrological conditions and the regulated/artificial cross-section, which further contributes to the natural deposition of particles in the section in question, upstream from the SHPP.

At the site of the SHPP, a new 50 cm high dam will create an impoundment with a maximum depth of 1.3 m. The impact zone will be at a distance of approx. 300 m. The impoundment will be built in an area covered by vegetation (on the banks of the Pesnica River riverbed) and will not extend in height to the lateral embankments along the Pesnica River riverbed, as these were not designed as embankments exposed to permanent impoundment.

The area of the Pesnica flood relief channel is initially cleared of alluvium which has settled in this area mainly on the convex bend of the riverbed. In order to control the deposition of large amounts of alluvium and at the same time to increase the capacity of the flood relief channel, which is a consequence of the reduction of the flow rate in the lower part of the Pesnica River from 30 m3/s to only 10 m3/s, it is important to clean the alluvium from the flood relief channel along the entire surface from Pesnica to the concrete part of the relief channel bed.

Intake

The water inlet for the turbine intake is a 9.0 m long and 5.0 m wide lateral intake structure. The intake structure is designed in two parts:

- a lateral intake made up of three sections where the dimensions of each section are w/h = 2.68/0.70 m and the total length of the intake including the two intermediate concrete columns is 9 m.

- a 4.2 m wide (14 m long) channel towards the power house, which becomes the power house channel immediately after the 75 cm high floor threshold. The outlet channel is equipped with a gate for cleaning debris.

The intake structure at the intake and the supply channel to the power house will be founded on covered ground over a foundation slab, which is also the bottom of the channel (at a ground elevation between 197.60 and 196.60 m). In the area of the intake, the bottom of the Pesnica River flood relief channel approx. 14 m long and approx. 4 m wide will be further deepened by approx. 1 m (to an altitude of 198.10 m).

Floating debris accumulated in front of the intake trash rack will be removed manually with sticks and rakes, while larger pieces will be removed with a hydraulic clamp mounted on a truck (hiap). A truck equipped with a hydraulic arm will be parked at the intake behind the wing wall and will load the alluvium from in front of the rack onto a truck-mounted skip. After the cleaning, the debris will be taken to a municipal landfill. According to the manufacturers, no additional fine rack is needed in front of the turbine, as the turbine is not sensitive to floating debris and conducts it to the water below.

The impoundment level will be at 199.80 m.s.l. The crown of the intake walls will extend in height up to the elevation of the surrounding terrain, i.e. up to 202.80 m.s.l. (above the 100-year water level of the Pesnica River). Walkable covers secured against opening will be placed on the top of the intake. The covers can only be opened with the gate lowered before the intake into the Archimedes screw.

The location of the intake structure itself, alongside the high-water embankment, has been chosen so as not to interfere with the clearance of the flood relief channel’s bed.

Hydro-mechanical equipment

The hydromechanical equipment of the intake part of the Pesnica SHPP comprises:

- Trash racks at the intake, made of 0.8 cm thick flat steel, on axial distance of 12 cm, with a total of 3x23 lamelles, 268 cm wide and 70 cm high, fitted into 3.5 m long side guides which allow each individual rack to be pulled out;

- Flat gate in front of the intake to the Archimedes screw, dim. 450/246 cm with associated guides, closing time max. 10 s (supplied with basic equipment, e.g. Vandezande);

- Gate of the floor drain of the intake structure, dim. 120/80 cm.

Channel for discharging sediments from the intake

A 75 cm high threshold is built into the bottom of the channel to clean sediments from the supply channel in front of the power house. The outlet channel is equipped with a gate 80 cm wide and 120 cm high. The outlet channel is approx. 15 m long and connects to the flood relief channel by breaking through the left wall.

Bag-shaped rubber dam

For the purpose of diverting the water into the water tract of the SHPP, a 27 m long bag-shaped rubber dam is foreseen at the spillway of the flood relief channel, which will allow the water level to rise by 0.5 m. When high-water conditions occur, it will be emptied thus lowering the water level to the level of the concrete channel bed, which will allow a smooth and unhindered passage of these waters through the flood relief channel. An associated hydraulic unit will be installed along the right side, elevated above the high-water mark.

The rubber dam will be founded on a concrete foundation slab, approx. 2.0 m wide, 27 m long, concreted to the existing concrete finishing of the flood relief channel. The anchors of the bag-shaped dam and the pipes for filling and emptying the rubber dam will be installed in the concrete foundation. A concrete shaft will be installed along the right bank of the dam to ensure the normal operation of the bag-shaped dam.

Power house

The Pesnica SHPP is a run-of-river power plant where the turbine runner is an Archimedes screw. It is installed in a concrete trough with a net width of 4.2 m, semi-circularly shaped on the underside, which also forms the turbine runner housing. The Archimedes screw axle is located between the elevation of the intake 199.80 and the outflow 193.06. The runner is mounted in two places, at the bottom on the outflow part and at the top in the generator area. The generator is located in an enclosed room/power house, while the Archimedes screw is in an outdoor trough. The trough of the Archimedes screw is covered with a prefabricated cover.

The power house structure is designed on top of the Archimedes screw channel and allows the installation of primary electro-mechanical equipment (generator, multiplier with a clutch, bearing, etc.). The building is 4.20 m wide, 5.30 m long and 2.50 m high, and is built into/immersed in the supply channel so that it is only raised by about 80 cm from the surrounding terrain. The ceiling of the power house structure is a prefabricated cover that allows personal access and transport of equipment to the inside of the building. It is envisaged that all the equipment is installed using a mobile crane. On the covering slab of the supply channel to the power house there is a transformer and a small container with dimensions of approx. 2.2m / 6m, in which the electrical equipment for the control and operation of the Pesnica SHPP will be installed.

The power house structure, in which the generator is installed, is founded on a pile mattress supported by concrete piles (Benotto piles or optionally ductile micropiles made of Ø170 mm diameter ductile pipes filled with concrete and grouted around the perimeter are foreseen). Similarly, the outflow part of the screw trough is also founded on a pile supported pile mattress. The two pile mattresses also take the full load of the channel with the installed Archimedes screw. The approximate size of the pile mattresses is 7x6 m. They are approx. 75 cm thick, supported by Benotto piles (or, alternatively, by driven micropiles made of Ø170 mm diameter ductile pipes filled with concrete and grouted around the perimeter). The piles extend into the marl stone base, which is at an elevation of between 190.5 m and 191.0 m.

There is an area next to the power house structure on the left hand side, just off the existing road, which can be consolidated during construction and used as a handling platform, which will be reclaimed once the installation is complete. This area provides a handling area for a mobile crane and a tow vehicle with a trailer during the installation of the equipment.

Access to the power house will be possible via the road leading along the embankment crest, while access to the Archimedes screw and the outflow part of the Pesnica SHPP will be possible via the existing road leading from the embankment crest to the berm at a nominal elevation of 195 m a.s.l. The embankment crest is safe from the impact of Pesnica River’s high waters and the water in the Formin HPP discharge channel.

A rectangular "U" shaped power house channel with a net width and height of 4.2 m/4.2 m and a floor length of approx. 12.0 m is routed from the prefabricated power house towards the Formin HPP discharge channel. The power house channel lies perpendicular to the Formin HPP discharge channel’s bed and is embedded in the bank at an inclination of 30°. After the power house channel, there is an outflow part with a bottom at 191.20 m.

The outflow from the power house is designed with respect to the Formin HPP tail water level at an elevation of 193.06 m, thereby minimally interfering with the clearance of the Formin HPP discharge channel.

The outflow structure will be founded on a pile mattress under which there are the Benotto piles (optionally micro piles made of Ø170 mm diameter ductile pipes filled with concrete and grouted around the perimeter). The pile mattress will be concreted onto a prefabricated trough that has been previously manufactured and delivered, which will be placed on top of the Benotto piles and will serve as formwork. All in-water concreting will be carried out in two phases, with formwork to seal and prevent cement milk from leaking into the Formin HPP discharge channel. In the event of cement suspension leaking into the water, this must be neutralised immediately.

The power house channel is designed according to the white bath principle. The thickness of the walls and panels will be 40 cm. The corners of the walls will be hydraulically adjusted. After the installation of the equipment (Archimedes screw), the space between the rectangular concrete trough, limited on the upper side by a separating steel sheet, will be filled with secondary concrete to provide the required gap to the turbine runner of the Archimedes screw. This section is installed in the bank at an angle of 30°.

Power house equipment

The basic characteristics of the turbine equipment are as follows:

Net head 			H = 6.74 m

Installed flow 			Q = 5.00 m3/s

Turbine power output 		P = 244 kW

Screw diameter 		D = 3.60 m

Turbine screw length	 	L = 13.5 m

The installation of a power unit with an Archimedes screw (e.g. Vandezande or similar) is foreseen. There are different types of Archimedes screw turbines available on the market as a finished product. The turbine was selected on the basis of the estimated installed flow, the available height and the slope of the terrain on which it will be installed. Another important constraint regarding turbine selection is the limitation of how much the turbine interferes with clearance in the Formin HPP discharge channel. For these reasons, a turbine with a 3.60 m screw diameter was selected as the most suitable in the first phase.

All the construction work on the facility was planned for the installation of a power unit with an Archimedes screws of various manufacturers, but the details without which it is impossible to foresee all the necessary construction work were based on the brochure documentation from Vandezande. This does not mean that the mentioned company is the only possible supplier of the power unit.

The power unit is delivered to the site in separate pieces (the turbine and the other part, which is the generator with all the auxiliary equipment) and anchors for installation in the prepared concrete trough and onto the generator foundation. The equipment is to be dry-assembled on partially prepared anchors in the concrete through and on the generator foundation. The trough and foundation shall be pre-executed by the LOT A Contractor in cooperation with the LOT TG equipment Supplier. The cooperation concerns the installation of anchors in the concrete structure. Installation, as well as all equipment delivery, is carried out by the Lot TG equipment Supplier and is carried out by mobile-crane directly from the trailer to the installation site. After installation and assembly of the turbine equipment, the space between the metal cladding of the turbine screw and the concrete trough is finely grouted with cement mortar, while ensuring the required gap between the trough cladding and the turbine screw blades. The works shall be carried out by the LOT A Contractor, as instructed and supervised by the LOT TG equipment manufacturer.

General requirements for electrical equipment

General

The equipment supplied under the contract must be new and of high quality, fit for its intended use, undamaged and in working order. The equipment shall conform to the classification to be given herein or be equivalent thereto, subject to the approval of the Client’s representative. Equipment intended for use for similar or identical purposes should be of the same manufacture and type.

The equipment selected will be a standard product of the LOT TG Contractor/equipment Supplier, fully designed and tested in accordance with the relevant standards. All equipment should have a CE certificate of conformity in accordance with IEC Directives 89/336/EEC, as of 3.5.1989.

The equipment shall be suitable for satisfactory operation under the conditions in which it is to be installed and shall operate satisfactorily under conditions of normal variations in power or voltage. It must also ensure safe operation and maintenance. Each piece of equipment or unit containing electrical equipment and wiring should be completely manufactured in the workshop. Wiring shall be neatly arranged and protected from mechanical damage, terminated in terminals mounted in junction boxes or enclosures on or near the unit and properly marked on both sides of each conductor.

Standard voltages

Low voltage AC circuits

All distribution systems, equipment and auxiliary power consumers must be adapted to be supplied from the

AC auxiliary power supply:

- Rated voltage: 3x400/231V ±10%, 50 Hz

- Earthing system: TN-C and TN-C-S

- Test voltage: 2.5 kV/min

- Minimum insulation resistance for new installations:

o between two phases: 400 kΩ

o to ground phase: 230 kΩ

Low voltage DC control and protection circuits

All distribution systems, control and protection circuits must be adapted to be supplied from the DC auxiliary power supply:

- Earthing system: ungrounded system, IT-K

- Test voltage: 1.5 kV/min

- Minimum insulation resistance for new installations: 220 kΩ

The control equipment uses 24 V DC locally, generated by 230 V AC/24 V DC converters.

Colour coding

In general, colour coding on control panels, electrical connections, etc., should follow IEC recommendations. Live parts of electrical connections shall be colour coded according to SIST IEC 60446:

| System | Conductor | Alphanumeric code | Symbol | Colour |
| --- | --- | --- | --- | --- |
| AC voltage systems | 1-phase | L1 |  | Black |
|  | 2-phase | L2 |  | Grey |
|  | 3-phase | L3 |  | Brown |
|  | Zero | N |  | Light blue |
| DC voltage systems | Positive | L+ | + | Red |
|  | Negative | L- | - | Blue |
|  | Zero | M |  | Light blue |
| Earthing and neutral in TN-C systems |  | PEN |  | Green/yellow |
| Protective earthing |  | PE |  | Green/yellow |
| Ground |  | E |  | Black/light blue |

This colour coding does not apply to conductor colours in single or multi-core cable connections.

Design of the devices

The equipment, including all auxiliary parts necessary for normal operation, must be constructed according to the latest state of the art, from unused materials and be completely free from defects.

Electric motors

All electric motors will be 3-phase short-circuit induction electric motors, unless otherwise specified. Also, all electric motors should be fully enclosed, fan-cooled, with IP 54 protection according to EN60034-5 (TEC 60034-5). Motors must comply with the requirements of the applicable standards in EN60034 (TEC 60034). Starting will be direct unless otherwise specified. All dimensions must comply with EN50347 and IEC 60072. All electric motors, including auxiliary and protective equipment, shall be capable of continuous full-power operation at a voltage between 90% and 105% of the rated voltage of the electric motor. The junction boxes of electric motors should be designed for cables or pipes to enter from below or from both sides. Flexible rubber cables should be used for the connection between the electric motors and the safety cut-off switch/junction box. Sealed ball or roller bearings should be used, except for small control motors, which may have tapered roller bearings. Ball or roller bearings that are not sealed should be lubricated using a low-pressure lubricator with the function of preventing over-lubrication. These bearings should have openings at the top and bottom for lubrication and lubricant drainage. Inaccessible bearings should be equipped with filling or drainage pipes. The insulation of the electric motor windings shall be of vacuum impregnation type. The insulation should comply with HD566 class F (IEC 60085) with a maximum temperature rise of 80°C at rated power.

Electrical enclosures

The equipment shall be constructed according to the latest state of the art with a minimum mechanical protection rating of IP67 for enclosures mounted outdoors, or IP 44 for enclosures mounted indoors, or as required in the Particular Technical Specifications and specifications for individual devices. The equipment shall have the required connections for earthing. Connection markings must be clear and prominently displayed. Easy access to terminals and servicing of equipment and its components must be ensured. The manual control and monitoring elements shall be installed at a height of 60 cm to a maximum of 180 cm from the finished floor height, in accordance with SIST EN 50274.

All equipment must be adapted for connecting cables from the upper and lower side or according to the requirements of the Particular Technical Specifications. The terminals must be positioned in such a way to allow easy access and connection. The enclosures shall be provided with suitable, properly sealed conductor plates and properly sealed cable glands for the intended cable cross-sections. Whenever it is required to connect auxiliary signalling contacts to a terminal block, the terminal block shall be designed as to enable easy (via potential bridging) connection of contacts for the purpose of supplying a common potential and/or grouping.

Terminals should be used that allow at least two parallel bridges.

All enclosures and cabinets intended to be installed to a wall shall be supplied with spacers on the back of the enclosure (at the points of attachment) which will allow them to be fixed to the wall with a minimum distance of 3 cm from the wall.

Each enclosure and cabinet shall have one or more earthing bars with a cross-section of at least Cu 50x5 mm in the area where the cable screens are to be earthed, to enable that proper earthing of the screen is carried out, in accordance with the recommendations on the limitation of overvoltages in electrical installations and on electromagnetic compatibility. The equipment in the enclosures shall enable earthing the cable screens over the entire surface of the screen. All equipment must be manufactured in such a way that short circuits cannot be caused by animals.

All installations, connections and cable inlets must be so designed as to prevent the outbreak of fire, its spread or any damage caused by fire.

To ensure uniformity on the facility, all enclosures and other equipment shall be fitted with terminals of the appropriate quality from a manufacturer such as Weidmueller, standardised according to the required types used and numbered with permanent numbers or markings. All wire connections must also bear element/terminal markings, and all elements in the enclosures must be marked according to the diagrams. For control and signalling circuits, terminals with reliable spring-loaded fixing technology shall be used.

All switchgear (circuit breakers, switches, automatic switches, etc.) must be of suitable quality, such as that manufactured by ABB, Eaton, Moeller, Schneider, Siemens or equivalent. Signal lights shall be of LED design.

All potential free contacts intended for signalling shall be of high quality, with gold-plated contact surface and minimum contact resistance, designed for reliable switching at 24 V DC/7 mA level. All auxiliary contacts must be wired to the terminals. The devices must be modular, made up of units suitable for easy transport and assembly. Components must be easily replaceable without special tools.

All enclosures shall be suitably protected against corrosion and finished in RAL7035. Deviation from this requirement may be approved by the Client if it is proposed by the LOT TG Contractor/equipment Supplier.

All equipment shall be designed to be easily installed and transported in the space shown in the illustrations.

All enclosures shall have a 100 mm high base or frame to be fixed directly to the concrete floor, as appropriate to the spatial requirements.

Each device must be provided with factory and type markings and nameplates to indicate its purpose and use in the Slovene language.

Parts of devices that will be permanently or occasionally at high potential must be protected against accidental contact and visibly marked as required by applicable regulations.

All enclosures and cabinets to be installed outside of the facility shall be made of stainless-steel sheet of a minimum AISI 316L quality. They shall be constructed with an additional stainless-steel canopy to prevent the penetration of rainwater.

EMC requirements

All metal parts should be joined together with a good electrical connection. Electrical enclosure/cabinet doors should be connected to the cabinet structure by the shortest possible earthing strap. Each electrical enclosure/cabinet will have a copper earthing terminal with connectors to connect the individual cubicles and equipment within the enclosure. The block will be installed across the full width of the enclosure. All structures, equipment, etc., should be connected to an earthing block that will allow connection to the hydroelectric power plant’s earthing system and to special earthing equipment. All electrical equipment enclosures should comply with the EMC requirements of EN61000 (IEC 61000).

Signalling and power cables should be laid separately from each other. To prevent interference, the cable groups should be spaced at appropriate intervals. Signalling cables should be gathered in the electrical enclosure on one level and not from several sides. Enclosures should be equipped with special EMC terminals to allow good earthing of the cable screens. The method of earthing the cable screens shall be approved by the Client's representative. Signal cable screens terminating in electrical/distribution cabinets should be earthed on both sides by using special clamps that completely enclose the cable.

Terminal blocks

All measuring and control cables should terminate in marked terminal blocks. Terminal blocks should be mounted in such a way as to allow easy connection. Terminals that have screws for direct pressure on the conductors will not be allowed. The terminals must allow a single part to be replaced without removing the entire row of terminals. There will be no more than two conductors in one terminal block.

The power and control circuits should be separated by intermediate plates or connected to separate terminal blocks. Power terminals should have covers. At least 10% spare terminals should be provided on each block. The terminal blocks should be selected in accordance with EN60947-7-1 (IEC 60947-7-1), they must be manufactured in accordance with the relevant standards. The terminal blocks of the control circuits shall be separable on both sides and shall be designed for connecting conductors up to 4.0 mm2.

Wiring

All internal wiring shall contain H07V-K copper conductors. Insulation shall be of fire-resistant polyvinyl chloride (PVC) or other approved fire-resistant material. The ends of conductors with insulation removed shall be fitted with compression sleeves. The LOT TG Contractor/ equipment Supplier shall ensure proper surface protection of the connections against oxidation and deterioration as a result of electrolytic corrosion.

In the case of cable connections, the cable cores must be numbered or colour coded in accordance with the HD SIST standard (equivalent to HD DIN VDE). All connections between pieces of equipment which run at least partially outside of enclosures, cubicles, housings, coverings, etc., shall be designed and implemented as cable connections. Cables with colour-coded conductor marking shall be used for power circuits. For signal, measuring and control circuits, cables shall be used with numbered conductors and screens providing at least an 80 % coverage. For cable connections for power circuits, cable type NYCY or NYCWY may be used. All connections must be permanently and correctly marked.

The conductors shall have the following minimum cross-sections:

- 2.5 mm2 for all electrical consumers (motors, heaters, etc.) and for secondary connections of current measuring transformers,

- 1.5 mm2 for other instrument wiring,

- 0.75 mm2 for signalling auxiliary contacts, etc.

- To identify internal wiring, the conductors shall be provided with identification plates with a printed mark. The plates must be installed in such a way that they do not come off when the conductor is unscrewed and removed from the terminal.

- The following categories of terminal blocks are prescribed:

  - terminal blocks for connecting auxiliary power supply with cables of up to 4 mm2,

  - current measuring terminals for conductors of up to 6 mm2 with short coupling possibility for current transformer circuits,

  - terminal blocks for measuring and control circuits, with the possibility of interconnection where required.

Terminations of appropriate dimensions for the thickness of the wire connections shall be fitted on all wired connections. The manufacturer shall ensure that the connectors are properly surface protected against oxidation and deterioration due to electrolysis. A torque wrench shall be used to tighten the fixing bolts.

Labelling of equipment and conductors

All enclosures, cabinets, panels, instruments, control equipment and complete wiring should be neatly and clearly labelled in accordance with the schematic diagrams and wiring diagrams. Nameplates must be placed in a prominent position. Nameplates must be fitted on the front and rear of the devices. All nameplates shall be of a uniform appearance and design, approved by the Client. The LOT TG Contractor/equipment Supplier shall ensure that the nameplates of each subcontractor are uniform throughout the supply under this invitation to tender. The requirements for the design of the nameplates and print will be determined by the Client. Element markings shall be in accordance with the HSE’s Internal Technical Standards. Labelling instructions will be provided to the LOT TG Contractor/equipment Supplier after signing the contract. Each major piece of equipment must bear a durable and visible manufacturer's nameplate with basic information on the manufacturer, serial number, date of manufacture and main technical data. Standard components (electric motors, contactors, etc.) must also bear the manufacturer's original factory nameplate.

The inscriptions on the nameplates (of enclosures, elements in enclosures, etc.) shall be legible, resistant to ageing and mechanical wear, and written in Slovene. The nameplates on low-voltage equipment enclosures shall be engraved with at least two coats of colour. All warning notices required for safe operation must be uniformly designed, prominently displayed and must be in Slovene. The plates and fittings shall be corrosion-resistant; this also applies to the cables used to attach them.

Cables

Wiring between electrical equipment should be carried out with cables of specified types and cross-sections. Cables should be laid on cable trays, in pipes, etc. Cables should be properly secured and at the entry point to the enclosure marked with PVC strips or rings. Yellow-green conductors should only be used as earthing conductors. Light blue conductors may only be used as neutral conductors.

Earthing

The enclosures and metal structures of all equipment supplied shall be properly connected to

the earthing system to be installed on site by the LOT TG Contractor/equipment Supplier  responsible for electrical equipment (turbine, generator, switchgear).

The primary purpose of earthing devices is:

* protecting people who come into contact with the equipment,

* protecting the device itself and other devices connected to it; and

* reducing electrical interference.

Based on the above, earthing systems are divided into:

a) protective earthing, i.e. earthing of those parts of installations which do not belong to the devices’ electrical circuits. These are usually isolated parts of the equipment where dangerous voltage can occur due to damage to the insulation;

(b) operational earthing, i.e. earthing of that part of the unit which is permanently or occasionally an integral part of the operating electrical circuit.

To ensure electromagnetic compatibility, one connection to a main equipotential bonding busbar should be provided in enclosures less than 300 mm wide, and two in wider cabinets. The connection shall allow the connection of a conductor with a cross-section of at least 70 mm2.

Equipment parameterisation

Any equipment supplied that requires parameterisation must be parameterised in principle according to the available input data. At the installation site, the pre-set parameters are then only adapted to the requirements of the installation site. If the equipment to be parameterised uses a digital application, the LOT TG Contractor/equipment Supplier is only obliged to hand the latter to the Client upon completion of the works.

Equipment for control and supervision

Such equipment, including its interconnections, shall be installed and tested in accordance with the same principles as those that apply to other equipment, as it forms an integral part. Listed below are specific requirements relating to certain control equipment components that are not further defined in the specifications.

Control switches, push-buttons and other equipment

Physical signals, signals produced by devices (analogue, digital) that will be installed outside and exposed to the elements, must have an adequate surge protection with galvanic isolation. Switching elements will be manufactured in accordance with EN60947-5-1 (IEC 60947-5-1). The selector and control switches should be of a rotary type. Change-over switches (selectors) and push-buttons should be provided with a sufficient number of positions, suitable handles and contact necessary for the intended functions. Impulse switches should be of a rotary type with return to neutral by means of springs or push-buttons. Change-over switches should be rated for 230 V AC or 24 V DC control voltage depending on the circuit in which they are used.

Display instruments

The instruments should be manufactured in accordance with EN 60051 (TEC 60051) and EEC 60473. They should be equipped with a long 250° scale with numbers on a white background. The external dimensions should be at least 72 x 72 mm. The accuracy grade should be at least 1.5% over the full length of the scale. The instruments should be able to be zeroed from the front. Ammeters and voltmeters shall be able to withstand a constant overload of 20%. The scales and nameplates of the instruments will be subject to approval by the Client.

Signal lights

Signal lights will be manufactured in accordance with EN60947-5-1 (IEC 60947-5-1). The lights shall be suitable for installation in panels and on enclosure doors and for appropriate voltages. Each light should have a removable cover that is not sensitive to the heat of the bulbs. Lights should be equipped with LED bulbs. Bulbs should be replaceable from the front. All bulbs must be of the same size and type.

Special requirements for electrical equipment

The subject of the project is the construction of a SHPP on the existing water infrastructure, the flood relief channel of the Pesnica River. A flow-through small hydroelectric power plant is planned with irreversible water withdrawal from the Pesnica River and its diversion to the Formin HPP discharge channel. The SHPP consists of the following parts:

- the SHPP’s power house with the power unit (an Archimedes screw turbine is used), the intake structure and the electrical equipment container,

- an inflatable dam to ensure the headwater water level of the SHPP (not in the scope of this Tender),

- a high-water membrane with a flat gate to ensure adequate flow rate in the Pesnica riverbed downstream of the site (not in the scope of this Tender),

- transformation (20/0.4 kV) and connection to the 20 kV switchgear at the Formin HPP (not in the scope of this Tender).

The electrical equipment of the SHPP will consist of the following parts:

- 20 kV MV switchgear (not covered by this Tender),

- 20/0.4 kV transformer (not covered by this Tender),

- electrical generator of the unit,

- frequency converter,

- LV equipment for generator circuit breaker and grid disconnection point,

- auxiliary power supply LV equipment,

- unit control equipment,

- communication equipment,

- LV power, signal, control and communication connections.

The electrical equipment of the SHPP is shown in a single-line diagram in the document HI1F---6E0100, as a suggestion. The Tenderer may propose a different arrangement of the equipment in the enclosures, which means that a revised single-line diagram must be submitted with the letter of tender. If the Tenderer proposes a different arrangement, the proposed arrangement must ensure a complete functionality as required by tender documents.

The limit of supply of equipment and installation under this LOT TG are the LV terminals on the 20/0.4 kV transformer. The scope of works under this contract includes all equipment from LV terminals on the transformer (including LV cable terminations) up to and including the power unit. The limit is shown in the illustrations (single-line diagram). The transformer, the 20 kV switchgear and the 20 kV connections are not subject of supply and installation under this invitation to tender. Under this LOT TG, the Contractor shall provide two outputs for auxiliary power supply of the remaining SHPP systems, one 3x25 A and one 3x20 A, as shown in the single-line diagram. For the communication connections, the Contractor shall provide ports on their equipment for connecting to higher-level control systems. The actual communication connections from the power unit’s controller and frequency converter to the higher-level controller in +CNQ01 shall be made by the Contractor under another tender.

Pesnica SHPP will be connected to the 20 kV distribution network at the existing 20 kV switchgear at Formin HPP. SHPP’s equipment as well as the entire SHPP must comply with the requirements of the SONDSEE (Official Gazette of the Republic of Slovenia No. 7/2021 of 19.1.2021), which forms part of this tender documentation together with its annexes. Depending on the output power of the unit and the connection to the 20 kV network, the SHPP must meet/ensure:

- the conditions for a type B of power generating modules,

- J-S1 reactive power characteristics,

- D-1 operating power characteristics,

- Z-Uf-B grid disconnection point protection.

All equipment supplied under this Tender must be certified and meet the requirements of Slovenian and European legislation and standards. The LOT TG Contractor/equipment Supplier shall provide declarations of conformity or performance for all equipment supplied.

MV switchgear equipment

The MV 20 kV switchgear will be located outside by the container next to the transformer and will be used to connect the SHPP to the electrical grid. It will consist of two metal-enclosed 24 kV cells in SF6 design. All actuators of MV switches will be manually operated. A standard switchgear with the following cells shall be used:

- a cable cell for connecting the 20 kV cable from Formin HPP,

- a transformer cell (equipped with a manually operated switch disconnector, fuses whose blow needle operates to trip the switch-disconnector, earthing switch and ready for cable connection).

The supply and installation of MV switchgear equipment is not the subject of this contract.

20/0.4 kV transformer

A standard transformer with a hermetically sealed boiler without a conservator is planned. The transformer will be located outside on a platform and will be enclosed by a mesh fence (2.5 x 2.5 cm) with a roof and a catch basin.

The supply, transport and installation of the transformer is not the subject of this invitation to tender.

Electrical generator of the unit

The electric generator, together with the gearbox and turbine, frequency converter and ancillary equipment, constitutes the power unit to be designed, supplied, installed and commissioned under this tender documentation.

The LOT TG Contractor/equipment Supplier must dimension the generator in such a way as to allow it to operate continuously at full power that the turbine is capable of providing, which means that all the unit’s devices (generator, gearbox, frequency converter, bearings, brake, shaft and turbine) as well as the auxiliary systems that are necessary (cooling system, etc.) for the normal continuous operation of the unit at full power must be dimensioned accordingly.

An asynchronous generator is to be installed, connected to the 0.4 kV, 50 Hz voltage level via a frequency converter. An asynchronous generator with the following data is foreseen:

        - Rated capacity (kVA):		according to the turbine power at the generator power

factor of 0.8

- Rated rotations: 		according to turbine and gearbox speeds

- Rated voltage:			400 V AC (or according to the frequency converter)

- Rated frequency:		50 Hz

- Mechanical protection		IP55

- Insulation level		F

The LOT TG Contractor/equipment Supplier may also supply a permanent magnet synchronous generator connected via a frequency converter or a conventional synchronous generator, whereby the excitation equipment, equipment for the electrical protection of the generator and excitation system and equipment for synchronising the generator with the grid must be supplied with the synchronous generator and the full functionality of the SHPP for permanent operation on the grid must be ensured. Regardless of the type of generator, it must meet the same requirements as the intended generator.

The generator shall be equipped with three thermal sensors (PT100) to measure the temperature of the generator windings.

The generator will be mounted on a concrete base of 0.9 x 1.5 x (0.17 to 1.42) m in a power house with planned dimensions of 3.0 x 4.4 m. The works described shall be carried out by the civil works Contractor under LOT A. The LOT TG Contractor/equipment Supplier shall check the dimensional condition of the concrete foundations prior to the installation of the power unit, where upon the LOT TG Contractor/equipment Supplier shall install the generator and all auxiliary equipment on pre-cast concrete (which was laid by the civil works Contractor under LOT A) and adjust the installation to the condition of the concrete. Prior to concreting the base, the LOT TG Contractor/equipment Supplier shall supply and install all anchors, if any, in the formwork, and fix them in such a way that they remain in position and do not move during concreting. The LOT TG Contractor/equipment Supplier shall provide a drawing of the turbine concrete shaft with concrete bases for the generator and the gearbox in their tender. The LOT TG Contractor/equipment Supplier shall also supply, together with the generator, ventilation/cooling equipment for cooling the generator and the gearbox, including control of the cooling system. The LOT TG Contractor/equipment Supplier shall also ensure that the temperature of the generator shaft, the gearbox and of all the bearings is being measured. Temperature data must also be available via Profinet communication to the higher-level control system.

Frequency converter enclosure +BAA01

The generator is to be connected to a 400 V AC, 50 Hz switchgear via a three-phase frequency converter which will be installed in a +BAA01 enclosure. The +BAA01 enclosure must provide at least IP42 mechanical protection and will be located in a container on the platform of the intake structure.

The three-phase frequency converter must comply with the SONDSEE requirements regarding the type of power-generating unit, reactive power characteristics and operating power characteristics.

The converter shall be dimensioned for the operation of the power unit at full power and shall provide adequate voltage and frequency on the grid side, and be equipped with an EMC/RFI filter for networks with an earthed neutral point (TN). In normal operation, the THD should be less than 3% (<3%).

The frequency converter must provide at least the following:

- mains voltage 3x/400 V, with the possibility of operating at ±10%;

- frequency 48 ... 63 Hz,

- continuous output current > generator current, at an ambient temperature of 40°C,

- rated power > generator output at an ambient temperature of 40°C,

- built-in electromagnetic interference (EMC) filter and filter according to EN 61800-3,

- control screen with text display for software operation.

- The frequency converter shall enable communication with the higher-level controller of the power unit for the purpose of exchanging operating data. Standard Profinet communication is used for communication. The set of data to be transmitted will be determined by the Client based on the technical data of the offered frequency converter.

In addition to voltage and frequency adjustment, the frequency converter must synchronise the power unit to the grid and provide the generator’s protection functions:

- voltage protection (over and under voltage),

- frequency protection (over and under frequency),

- current protection (overcurrent and short-circuit),

- reverse power protection,

- voltage asymmetry protection.

The frequency converter shall enable communication with the power unit’s control system via Profinet, Profibus or Modbus communication protocol. Following the communication, it must send the following data to the higher-level control system:

- power unit’s operating power,

- reactive power,

- apparent power,

- current,

- voltage,

- power factor,

- the temperature of the frequency converter,

- alarms in case of protection function activation,

- alarms in case of abnormal conditions; and

- alarms in case of malfunctions.

The frequency converter will receive the following commands from the power unit’s control system via Profinet communication:

- shut-down and

- start-up.

The three-phase frequency converter ACS880-17-0505A-3 from ABB is planned. The Tenderer may also offer a three-phase converter of another type or manufacturer that is technically equivalent to the prescribed frequency converter.

If the converter does not enable the application of the protection functions, a suitable protective relay must be supplied to allow the application of the above protections.

The LOT TG Contractor/equipment Supplier shall demonstrate compliance with SONDSEE for the converter and register the converter on the list of approved equipment with the SODO electricity distribution system operator.

LV enclosure for generator circuit breaker and grid disconnection point +BAA02

In accordance with the single-line diagram, between the transformer and the three-phase frequency converter at the 0.4 kV, 50 Hz level, the Pesnica SHPP will be equipped with a +BAA02 enclosure in which a generator circuit breaker, grid disconnection point, grid disconnection point protection, current transformers for measuring production and auxiliary power consumption, and auxiliary power supply equipment will be installed. The +BAA02 enclosure will be located in a container on the platform of the intake structure.

The +BAA02 enclosure shall be equipped with an emergency stop button which stops the operation of the power unit via the control system.

All auxiliary contacts of switches and circuit breakers shall be wired to the terminals in the enclosure for connection to the control system.

Grid disconnection point switch and generator circuit breaker

The grid disconnection point switch and the generator circuit breaker shall enable remote switching on/off and spring winding. The switches shall be dimensioned for a full load at the power unit’s full operating power and a power factor of 0.8, and be capable of tripping the expected short-circuit current according to the contribution of the network and the power unit.

Current transformers for measurements

The +BAA02 enclosure shall be equipped with current transformers for measuring gross electricity produced and current transformers for measuring auxiliary power supply. The current transformers shall be wired to a metering set that allows separation. When the equipment is supplied, the windings of the current transformers shall be short-circuited. The current transformers must be certified and calibrated, for which the LOT TG Contractor/equipment Supplier must provide the relevant documentation in accordance with metrology legislation.

Current transformers with the following data shall be used:

- Current transformers -T2 (gross production)

  - turn ratio: 500/5/5 A

  - nominal power of a winding: 5/5 VA

  - accuracy class: Fs

- Current transformers -T4 (auxiliary power supply)

  - turn ratio: 40/5/5 A

  - nominal power of a winding: 5/5 VA

  - accuracy class: Fs

Current transformers for auxiliary power supply shall be installed in such a way that the total auxiliary power supply of both the power unit and of the appliances not included in the scope of this supply is measured.

Meters for measuring production and auxiliary power supply are not subject of supply under this invitation to tender and will be provided by the Client under another invitation to tender.

Grid disconnection point protection

In accordance with the requirements of SONDSEE and the Annexes, the grid disconnection point must be equipped with a protective relay that will provide the following protective functions:

- voltage protection (over and under voltage),

- frequency protection (over and under frequency),

- current protection (overcurrent and short-circuit),

- earth fault protection.

Delivery point

The delivery point is planned to be at 400 V in accordance with the design conditions.

The electricity will be measured at the 400/230 V voltage level with the following two meters:

- meter for gross energy produced located at the generator output after generator switch,

- meter for auxiliary power supply.

The -T1 and -T2 current transformers and the metering set for connecting the current and voltage circuits of the meters will be installed in the +BAA02 enclosure and are part of the scope of supply under this Tender. All internal connections in the +BAA02 enclosure are also included in the scope of this contract.

The meters will be installed in the +CNQ01 enclosure and are not part of the scope of supply under this Tender, nor is the connection of the meters from the +CNQ01 enclosure to the metering sets in the +BAA02 enclosure.

Auxiliary power supply equipment

As part of the auxiliary power supply equipment, the LOT TG Contractor/equipment Supplier shall supply the equipment, including connections, necessary to power the devices and auxiliary systems supplied under this Tender. The auxiliary power supply equipment of the power unit and the auxiliary systems of the power unit will be installed in the +BAA02 enclosure. For supplying power to devices not subject of supply and installation under this Tender, the LOT TG Contractor/equipment Supplier shall provide two three-phase outputs with fuses/circuit breaker (3x25 A and 3x20 A) in the supplied +BAA02 enclosure.

The LOT TG Contractor/equipment Supplier shall supply and install all the auxiliary power supply equipment for Pesnica SHPP, and shall inspect, test and commission the equipment after its installation.

Unit control equipment and communication equipment +CNA01

The LOT TG Contractor/equipment Supplier shall supply and install, within the scope of this contract, control equipment and communication equipment necessary for the management and control of the power unit and the unit’s auxiliary equipment. The power unit’s control equipment will be installed in the +CNA01 enclosure and is supplied under this invitation to tender. The enclosure shall also be equipped with the appropriate power supply equipment for the power unit’s controller and communication equipment for communication with the plant's higher-level controller. The LOT TG Contractor/equipment Supplier shall also develop, install on the controller, test and commission the software (software applications) of the power unit’s control system, to ensure full functionality of the power unit, including its auxiliary systems. The power unit’s control equipment shall enable automatic start-up and shut-down of the unit and manual operation of individual unit’s devices; however, it shall not allow the power unit to be connected to the grid without synchronisation conditions being met.

To control and monitor the high-water membrane equipment, inflatable dam, water level for the high-water membrane and the MV switchgear, a transformer power plant controller will be in located a separate +CNQ01 enclosure which will also be the master of the power unit’s controller. The equipment for the +CNQ01 enclosure is not covered by this tender documentation and will be procured by the Client under a separate invitation to tender.

The power unit’s controller will communicate with the plant's master controller using the Profinet, Profibus or Modbus communication protocol.

The LOT TG Contractor/equipment Supplier shall ensure the following signals (information) which will be sent via communication to the plant's higher-level control system:

- power unit’s operating power,

- power unit’s reactive power,

- power unit’s apparent power,

- power factor,

- current in all three phases,

- generator voltage,

- power unit’s status (running, paused, starting-up, shutting-down...),

- frequency converter diagnostics,

- head water level,

- tail water level,

- position of the grid disconnection point - open,

- position of the grid disconnection point - open,

- grid disconnection point protection - activated protection (alarm),

- position of the generator circuit breaker - open,

- position of the generator circuit breaker - closed,

- position of the auxiliary power supply switch - open,

- position of the auxiliary power supply switch - closed,

- generator temperature (all three probes),

- gearbox temperature,

- temperatures of all the bearings,

- generator shaft temperature,

- final position of the safety gate - open,

- final position of the safety gate - closed,

- position of the measurement safety gate,

- generator shaft cooling system - in operation,

- failure of fuses/circuit breakers of the power unit’s auxiliary power supply,

- all alarms to be generated on the equipment that have to be supplied under this invitation to tender (power unit, frequency converter, auxiliary supply, protection, etc.),

- power unit’s failure after electrical protection (either from a frequency converter or a separate relay).

The plant’s master controller will send the following commands to the power unit’s controller via communication:

- power plant start-up,

- power plant shut-down,

- data on the desired reference power (depending on the operating mode).

The plant’s master controller will send the following commands to the power unit’s controller over the wired connection:

- quick shut-down of the power unit

Measuring water levels

The LOT TG Contractor/equipment Supplier shall supply and install a system for measuring the water level of the power plant’s head water and the tail water. The water level probes shall be connected to the power unit’s control system in the +CNA01 enclosure to be supplied by the LOT TG Contractor/equipment Supplier under this Tender. The LOT TG Contractor/equipment Supplier shall supply all the necessary equipment including surge protection of signals and power supply of the measuring probes for the full functionality of the measuring system.

Cable connections

All cable connections, including power, signal, control, measuring and communication connections, between the equipment to be supplied and installed under this contract fall within the scope of supply, installation and testing under this invitation to tender.

Power connections

The limit of supply and installation of the power cables towards the grid connection point shall be the low-voltage terminals of the 20/0,4 kV transformer.

The LOT TG Contractor/equipment Supplier shall supply and install cables, cable terminations and cable accessories for all connections up to and including the limit, and the LOT TG Contractor/equipment Supplier shall inspect and test all the cables in accordance with Slovenian legislation (“Rules on requirements for low-voltage electrical installations in buildings" and TSG-N-002).

Signal and control cables and cables for measuring circuits

The scope of supply and installation includes all signal and control cables and cables for measuring circuits that will be used on site for internal connections for the transmission of signalling, data, measurements and control signals. The supply and installation also includes signal, control cables and cables for measuring circuits for the operation of the power unit and auxiliary equipment, as well as cables for the measurement of all water levels, including the water level for the high-water membrane.

After the installation of the cables has been completed, the LOT TG Contractor/equipment Supplier is obliged to inspect and measure the cables (checking the conductivity of the conductors and the insulation resistance of the cables).

Communication connections

The LOT TG Contractor/equipment Supplier shall supply and install all communication connections, both fibre optic and copper, as part of the equipment supplied and installed under this Tender. The limit of the supply and installation of the communication connections is the communication port of the power unit’s controller, intended for communication with the power plant’s higher-level controller.

Communication connection from the power unit’s controller to the power plant’s higher-level controller and onwards to the Formin HPP is not in the scope of this Tender.

The LOT TG Contractor/equipment Supplier is obliged to inspect all communication connections and perform the relevant measurements.

Execution of works

Detailed descriptions of civil works can be found in LOT A. At this point, we are simply pointing out the time constraints of the civil works on site.

Time constraint for works

Civil works for the construction of the Pesnica SHPP next to and in water can only be carried out from 01.07. to 30.11. Only works that do not affect water quality and the water regime in the Pesnica River and the Formin HPP discharge channel can be carried out throughout the year. All works may only be carried out in coordination with Ormož Fishing Society. (ZZRS, No. 4202-27/2012/17 of 29.05.2019), see also partial water permit (No.: 35523-2898 2013 ARSO).

Contractors and equipment suppliers involved in construction

Construction of the Pesnica SHPP requires a multidisciplinary approach to the construction of all facilities. The tender documents for the whole project are thus divided into four lots, namely:

- LOT A, comprising the works in accordance with the tender documents for the nominated L scope of works, is given in LOT A,

- LOT E, comprising electrical installation works except those electrical equipment, electrical installation works and equipment related to the power unit equipment covered by the present tender documents in LOT TG,

- LOT HMO, comprising the supply and installation of hydromechanical equipment except for the safety gate before the intake into the turbine shaft (which is the subject of the present tender documents under LOT TG), and

- LOT TG, comprising the supply and installation of a power unit and a safety gate in accordance with the tender documents for the present LOT TG, which also describe the supply limits between LOT TG and LOTs A, E and the HMO.

The Contractor who will carry out the works in accordance with the tender documents under LOT A will be the lead Contractor at the construction site of the Pesnica SHPP.

Cooperation between the contractors on the individual LOTs shall be by prior agreement, through exchange of documentation and on-site cooperation. It is very important for LOT TG that all the necessary documentation, on the basis of which detailed design documentation for the foundation of the equipment, for the design of the turbine shaft structure, for the connection to the electricity grid, etc., will be drawn up, is delivered to the Client in the first phase.

The cooperation between the individual contractors and the equipment Supplier has already been partially described in the previous text, but here we highlight the installation of the equipment and anchors and the grouting of the concreted parts of the equipment, such as the installation of the gate guides and the grouting of the area under the turbine runner cladding.

At the time of construction, the LOT A Contractor shall prepare the formwork and lay the reinforcement, after which the LOT TG equipment Supplier shall install and fix the anchors in the formwork before concreting the concrete structure which is done by the LOT A Contractor. Subsequently, the LOT TG Contractor shall install the equipment and the LOT A Contractor shall carry out the fine grouting of the concreted parts of the equipment under the technical requirements supervised by the LOT TG equipment Supplier.

Technical data

All equipment must be new, suitable for the installation site and compliant with relevant Slovenian legislation, rules, regulations, technical guidelines, standards (EN, SIST, IEC) and the requirements for placing equipment on the market.

Power unit

Basic data:

- Flow rate: 					Qi=5m3/s

- Elevation of the power unit axle above:	199.80 m a.s.l.

- Elevation of the power unit axle below:	193.06 m a.s.l.

- Normal head water elevation:			199.80 m a.s.l.

- Raised head water elevation:			201.70 m a.s.l.

- Nominal tailwater elevation:			193.06 m a.s.l.

- Minimum tailwater elevation:			191.00/190.00 m a.s.l.

- Power unit’s output power:			244 kW

- Outer diameter of the runner: 		3.6 m

- Total length of the power unit (turbine, bearings, clutch(s),

- multiplier, generator and brake):		18.15 m

- Turbine runner length:			13.5 m

- Inclination angle of the power unit: 		30°

- Runner rpm:					22.6 min-1

- Runner/cladding gap:				max. 10 mm

- Total weight:					max. 42 t

- Noise level at 1 m:				max. 70 dB

Turbine version with Archimedes screw

Turbine design:

The turbine structure consists of a turbine runner (Archimedes screw) placed in a trough and grooved at the top and bottom ends.

Design stage:

The Supplier shall prepare project design for execution, workshop drawings and as-built drawings, and the operation and maintenance documentation.

Archimedes screw body:

The Archimedes screw body is made of a tube, which is the shaft to which watertight screws are welded. The helix screw(s) and shaft that together form the Archimedes screw are made of S355 (St37- 2).

A rubber lining on the inlet and outlet edges of the helix screw protects the edge of the helix screw from sharpening and thus prevents injury to the fish.

The structure must be dimensioned for at least 500,000 operating hours.

Trough

The trough, which is also the supporting structure, is curved in the shape of the turbine runner/Archimedes screw and is welded in S235 sheet steel. Min. sheet thickness is 4 mm. The outer part of the trough is an RC structure (prepared in LOT A) in which the metal part of the trough is embedded and the middle part is filled with cement mortar for grouting (carried out by the LOT A Contractor).

The protection of the rotating part of the Archimedes screw turbine is provided by a removable protective cover attached to the top of the trough (according to description in LOT A).

Upper bearing:

The bearing housing is screwed with its base slab into the bedding in the floor slab of the concrete foundation. The upper bearing is made with a radial-axial bearing and allows the runner to be centred according to the geometry of the trough. The bearing is lubricated with biodegradable grease applied by an automatic lubricant dispenser. The entire bearing structure is corrosion-protected.

The bearing must be dimensioned for at least 200,000 operating hours.

Lower bearing:

The bearing is mounted on the transverse beams as a load-bearing structure. The bearing has a built-in sensor to detect the presence of water in the oil. The sensor is connected to the control panel. The entire structure is corrosion-protected. The lower bearing is made with a radial bearing. The design of the bearing shall be such that it allows the runner to be centred with regard to the trough, while compensating for any temperature and load shifts/stretches of the structure.

The bearing housing is watertight and has a built-in water and temperature sensor; the data is displayed on the control panel, where data storage is possible. The bearing is lubricated with biodegradable oil. The bearing must be dimensioned for at least 200,000 operating hours.

Corrosion protection:

All external surfaces in contact with water

Surface preparation:

- degreasing surfaces with an organic solvent or a mixture of organic solvents;

- sandblasting untreated surfaces in Sa 2 ½ quality according to ISO 8501-1/1988.

Base coating:

- epoxy binder based two-component primer with a

high zinc powder content, 50 m, e.g. SIKACOR ZINC R (FRIAZINC R) or equivalent.

Intermediate coating:

- epoxy resin-based two-component coating, 2 x 180 m., e.g. SIKA POXICOLOR SW RAL 7032 or equivalent.

Final coating:

- two-component coating based on epoxy resins and polyurethane, 1 x 40 m, e.g. SIKACOR EG5 RAL7042 or equivalent.

- total thickness: 450 m.

All internal surfaces not in contact with water

Surface preparation:

-  degreasing surfaces with an organic solvent or a mixture of organic solvents;

-  sandblasting untreated surfaces in Sa 2 ½ quality according to ISO 8501-1/1988.

Base coating:

- epoxy binder based two-component primer with a

high zinc powder content, 50 m, e.g.: SIKACOR ZINC R (FRIAZINC R) or equivalent.

Final coating:

-  epoxy resin-based two-component coating, 1 x 180 m., e.g. SIKA POXICOLOR SW RAL 7042 or equivalent.

Total thickness: 230 m.

Power transmission (multiplier and clutches)

Clutch:

The power unit will be fitted with an elastic toothed clutch (three-piece) which meets the quality and durability standards of, for example, Siemens-Flender.

The basic requirements for the clutch are:

- Rated torque:	150 / 7.7 kNm

- Safety factor:	2/2.6

Type of gearbox - multiplier:

The gearbox - multiplier is designed as a gear drive that must be dimensioned for at least 100,000 operating hours. It must meet the quality and durability standards of, for example, Siemens.

As a minimum, the gearbox must meet the following conditions:

- Rated torque:	240 kNm

- Safety factor:	2

Secondary clutch:

Elastic toothed clutch (two-piece) which meets the quality and durability standards of, for example, Siemens.

The secondary clutch shall meet the following characteristics:

- Rated torque:	7.7 kNm

- Safety factor:	2.6

Safety brake

A brake with a hydraulic thruster and a separate hydraulic unit is planned. The performance must be comparable in quality and durability to Siemens or equivalent products and must satisfy at least the following two conditions:

- Rated torque:	8.2 kNm

- Safety factor:	> 2

Safety gate

Safety gate; designed as a sliding gate with guiding elements made of wear-resistant special plastic; one-sided hydraulic actuator; hydraulic cylinder is fitted with a special seal kit for biodegradable hydraulic oil (e.g. Panolin HLP Synth 32), stop valves at the inlet and outlet of the hydraulic cylinder; gate sealed on 3 sides: side: seals in angled profile, bottom: flat seal; connection strips: hot-dip galvanised; guide frame made of steel U-profile, hot-dip galvanised; preparation for installation of a heating device for the guides (self-regulating heating rods); system allows emergency closing; the gate closes completely by its own weight in the time prescribed by the generator manufacturer for safe operation.

Width:		4.83 m

Height:	2.46 m

Double-acting stroke cylinder mounted directly on the steel frame.

Hydraulic unit

A compact hydraulic unit shall be supplied for the purpose of controlling the safety gate. The unit shall consist of a hydraulic gear pump driven by an AC asynchronous electric motor. The pump has an operating pressure of 130 bar. All the necessary control elements required for the correct and safe functionality of the hydraulic unit (solenoid valves, pressure switches, throttle check valves, etc.) shall be supplied. The unit shall also be equipped with measuring elements such as: oil level gauge with analogue output, oil temperature gauge, pressure switch for measuring oil blockage... Suitable hydraulic oil heaters shall be provided. The oil tank must be properly filled with a biodegradable hydraulic oil, such as Panolin HLP Synth 32. All bolted connections and pipe connections shall be galvanised. Hydraulic hoses running to the drive cylinders shall be fitted with appropriate UV protection. The hydraulic unit is delivered fully equipped and ready for use.

Services covered by this invitation to tender

Supply of equipment

The scope of supply shall include all the necessary equipment, devices and materials for the power unit and other SHPP installations, in accordance with the requirements of this invitation to tender. Supply is made to the construction site which means that the prices are prices for delivery to buyer/construction site.

Installation, testing, commissioning and training of the Client's personnel

The scope of installation and commissioning includes all equipment, devices and materials supplied under this invitation to tender. The LOT TG Contractor/equipment Supplier shall appoint a responsible head of works for the works covered by this tender documentation, who meets the requirements for a responsible head of works under Slovenian law.

The LOT TG Contractor/equipment Supplier must ensure the installation of the power unit (generator, multiplier with both clutches, brake and Archimedes screw with housing and bearings) in a concrete trough, including the power house and discharge part, with a floor length of approx. 20.95 m and a width of approx. 4.10 m. The Supplier shall provide all the necessary assembly equipment, including cranes, transporters, conveyors, measuring equipment and small assembly material, which shall be included in the tender price. The LOT TG Contractor/equipment Supplier shall also provide all the necessary equipment and personnel to carry out the relevant tests (commissioning and tests for SONDSEE compliance), which must be included in the tender price, including all the costs (transport, accommodation, daily allowance, etc.).

Measuring equipment must be calibrated and certified.

Upon completion of the tests and commissioning of the power unit and handing-over of the technical and supporting documentation of the power unit, the power unit will be handed over to the Client for trial operation. During trial operation, the LOT TG Contractor/equipment Supplier shall also provide training to the Client's personnel in the operation and maintenance of the equipment to the extent required by this Tender. The training shall be carried out at the installation site and/or at the Client's premises. Training for up to 15 employees of the Client is foreseen.

The LOT TG Contractor/equipment Supplier shall cooperate and supervise the grouting of the turbine cladding in the concrete trough. It shall also adjust the turbine cladding and the turbine screw before grouting the turbine cladding, and shall check the gap and other dimensions of the turbine cladding and the turbine screw during the grouting process.

Documentation

The LOT TG Contractor/equipment Supplier shall prepare design documentation (called factory documentation) for all the equipment, devices and materials supplied, which shall be the basis for the designer to produce the detailed design documentation. The LOT TG Contractor/equipment Supplier shall also prepare installation instructions, operation and maintenance instructions, proof of reliability (DZO) and other documentation as follows. The factory documentation must be prepared at the level of detailed design documentation in accordance with the Slovenian Building Act, the Rules on the detailed content of documentation and forms related to construction and professional rules (IZS), or any applicable law or regulation that will replace the above-mentioned law or regulation.

The LOT TG Contractor/equipment Supplier must deliver the following documentation to the Client at the time of the Tender:

- Basic technical data of the structure with dimensions of the equipment and the required gap next to the equipment, weights shown in the text and on the drawings

- Catalogue material

- List of recommended parts

- A technical description demonstrating that the technical requirements are met

- Tender documentation with completed details on equipment characteristics

- Transport dimensions and space required at installation

Within one month after introduction to work, the LOT TG Contractor/equipment Supplier shall hand over the following documentation to the Client:

- Detailed design documentation (electrical and mechanical)

- Workshop drawings

- Drawings with dimensions drawn, application of force drawn, magnitudes of the forces exerted by the equipment on the foundations when the power unit is operating under normal or emergency conditions and when the power unit is paused

- Drawings of the equipment supplied, showing the level of installation in the concrete structure and the performance requirements for the concrete structure(s)/foundations

- The technology (technical descriptions, procedures, recipes, control procedures at the time of grouting) for grouting the turbine cladding in the concrete trough

At a minimum, the following scope shall be required for the preparation of the documentation.

In the field of electrical engineering (electrical design), the documentation for all enclosures and interconnections for full functionality of the power unit must be produced. The electrical design must be divided into individual folders, with each enclosure in its own folder. The folders of the electrical design must contain at least the following content:

- technical report,

- single line diagram,

- diagrams developed,

- terminal blocks,

- cable lists,

- list of equipment for each enclosure,

- functional description and functional specification (only in the control folder - +CNA01 enclosure).

In the field of mechanical engineering, the documentation shall include a mechanical engineering design at the level of workshop drawings for the whole power unit and safety gate. In the design, the drawings shall show and the text shall describe all the dimensions of the power unit and the safety gate. The workshop drawings shall show the structure assemblies, the details of the finishing of the bill of materials and everything else necessary for the execution and installation of the structures.

The structural design shall show all the points on the structure through which loads are transmitted to the civil structures and foundations. All loads caused by the structures supplied in this LOT TG shall be entered on the drawing and described in the text. A drawing showing the concreted parts and anchors and describing any anchoring and grouting requirements for the equipment shall be attached.

The documentation must show the location of the power unit in the area, the characteristic axes of the mechanical structures, the boundary with the concrete structure, as well as the nominal elevations of the upper and tail water level. This documentation must be handed over to the Client for review within one month after introduction to work, as it is the basis for the preparation of the design documentation for civil structures.

The design documentation (factory documentation) must be submitted to the Client for review. The Client shall examine the documentation within 15 days and return it to the LOT TG Contractor/equipment Supplier with a report and status. If the documentation is approved with status A, the LOT TG Contractor/equipment Supplier may start the production of the equipment in accordance with the approved documentation. If the Client has comments and observations on the documentation, they will return the documentation to the LOT TG Contractor/equipment Supplier for correction and give the documentation a status B. The LOT TG Contractor/equipment Supplier shall then have 15 days to revise the documentation and provide clarifications to the Client and return the documentation with clarifications to the Client for another review. In all cases, the LOT TG Contractor/equipment Supplier is fully responsible for the adequacy of the documentation and the proper functioning of the power unit’s equipment, regardless of the comments and observations made by the Client. The validation process of the design documentation must be completed no later than 90 days after the introduction to work.

When preparing the documentation, the LOT TG Contractor/equipment Supplier is obliged to comply with HSE’s technical standards, which will be provided by the Client upon signature.

Furthermore, the LOT TG Contractor/equipment Supplier shall hand over the following documentation to the Client within the following deadlines:

- installation instructions - 60 days before the start of installation,

- programme and protocol (reports) of the commissioning tests - 60 days before the start of the commissioning tests,

- programme and protocol (reports) of SONDSEE compliance tests (Official Journal of the RS, No 7/21 and 41/22) - 60 days before the start of the commissioning tests,

- operating and maintenance instructions - 30 days before the start of the commissioning tests,

- detailed design documentation with corrections (corrections in red) - 7 days after completion of the commissioning tests,

- completed commissioning test reports - 7 days after completion of the commissioning tests,

- completed SONDSEE compliance test reports - 7 days after completion of the tests,

- proof of reliability documentation - 14 days after all tests have been completed,

- as-built documentation - 30 days after completed commissioning tests.

During the execution of the works, the LOT TG Contractor/equipment Supplier shall keep a construction logbook and a book of measurements in accordance with the Rules on construction sites (Official Gazette No.  55/08, 54/09 - corrected, 61/17 - GZ and 199/21 - GZ-1) or any applicable regulation that will replace these rules.

Prior to the actual installation of the equipment, the LOT TG Contractor/equipment Supplier shall deliver to the Client and the Supervisor declarations of conformity or declarations of performance or other documents proving the conformity of the equipment, devices and materials with Slovenian and European legislation. No equipment, devices or materials may be installed without these documents.

The LOT TG Contractor/equipment Supplier shall measure the installations in accordance with the requirements of TSG-N-002 and TSG-N-003, measure the communication connections, both copper and fibre, and commission the equipment upon completion of the installation and measurements. The LOT TG Contractor/equipment Supplier shall prepare a programme and protocols for the measurement, commissioning and testing of the SHPP, which shall be completed on an ongoing basis during the commissioning and testing.

The LOT TG Contractor/equipment Supplier shall develop software applications for the control system, and parameterise all the equipment and devices supplied under this invitation to tender. For the control of the high-water membrane gate, the inflatable dam and the signalling of some devices supplied under other contracts, the LOT TG Contractor/equipment Supplier will receive a functional description from the Client, which they must take into account in the development of the software application for the control of all SHHP systems. The LOT TG Contractor/equipment Supplier is obliged to deliver the relevant documentation and to carry out the appropriate equipment tests to demonstrate compliance of the entire SHPP at the tender boundary with the requirements of SONDSEE and the requirements of the electricity distribution system operator.

The LOT TG Contractor/equipment Supplier must draw up the proof of reliability documentation in accordance with the Rules on the detailed content of documentation and forms related to construction.

The LOT TG Contractor/equipment Supplier shall deliver all the above documentation in four (4) hard copies, an electronic copy in PDF format and an electronic source format. The proof of reliability documentation shall be submitted in one (1) hard copy only, in electronic PDF format and in an active format. The LOT TG Contractor/equipment Supplier must also hand over the programme (software applications), including all comments.

Documentation is charged as follows:

- completed factory documentation - 80% of the value of the documentation position,

- completed tests and submitted commissioning and measurement reports - 3% of the value of the documentation position,

- completed tests and submitted SONDSEE compliance reports - 2% of the value of the documentation position,

- completed operation and maintenance instructions - 5% of the value of the documentation position,

- delivered detailed design documentation - 5% of the value of the documentation position,

- completed and delivered proof of reliability documentation - 5% of the value of the documentation position.

Completed and delivered documentation means that the documentation has been reviewed and approved by the Client.

Spare Parts

The Tenderer for the supply and installation of equipment under LOT TG shall prepare a list of spare parts recommended to be supplied with the equipment. The Client will decide which of the spare parts to order together with the power unit based on the list of the recommended spare parts. When evaluating and comparing tenders of different equipment suppliers, the prices of spare parts are not taken into account in the tender price and thus do not influence the selection of the LOT TG equipment Supplier.

Warranty maintenance

The Tenderer must provide a programme for warranty maintenance during the warranty period. The programme shall specify the works, procedures and materials that the Contractor/Supplier will carry out as warranty maintenance. The programme must be prepared on a year-by-year basis for the entire warranty period.

Warranty maintenance is offered as optional in the tender. The Client reserves the right to order or not to order warranty maintenance.

Warranty maintenance shall not be included in the value of the tender for the purpose of selecting the most advantageous Tenderer in the calculation of the criteria.

Commercial terms for the supply and installation of equipment

Price parity:

ex buyer/construction site

Construction deadlines/time schedule

Execution design 1 month after the introduction to work, with the delivery of workshop documentation which contains all the dimensional data of the power unit, power unit’s foundation data, data on power unit’s anchoring in the concrete structure, all loads from the power unit to the concrete bases and foundations, to the Client.

Delivery and installation deadlines:

• The safety gate shall be delivered to the construction site and installed

4 months after the introduction to work

• The power unit (turbine, multiplier, generator, control and management...) shall be supplied and installed

5 months after the introduction to work

.

• The power plant must be commissioned after completion of work on all LOTs and no later than

30/10/2023

If the building permit is not obtained within the time frame foreseen, the installation of the equipment on site and the commissioning of the power plant will be delayed accordingly, and the Client will inform the equipment supplier accordingly.

Indicative implementation deadlines are given above. More specific deadlines will be agreed separately between the Client and the Contractor/Supplier. The Contractor/Supplier shall send to the Client, within 5 days after concluding the Contract, a detailed time schedule for the execution of the works for their review, coordination and approval. Once coordinated and approved, it shall become an integral part of this contract and the time limits in the schedule shall become the contractual time limits.

Start-up

Start-up:

The commissioning of the unit follows immediately after completion of the installation of the equipment under LOT TG and all other work under LOT A, LOT E and LOT HMO. During the commissioning, a commissioning report shall be drawn up and signed by the contracting parties – LOT TG equipment Supplier and the Client. If minor deficiencies are found which could not be corrected during commissioning, but which do not affect the functionality of the unit, the LOT TG Contractor/equipment Supplier shall remedy them within 14 working days. However, if deficiencies affecting the functionality of the unit are established, the operation can only start after they have been corrected.

Only after successful commissioning, correction of all deficiencies and a handover of all the necessary documentation, the facility is deemed handed-over to the Client.

VGP Maribor: Pesnica flood relief channel, project no.: 940/4-83, February 1983

ARSO: Partial water use permit no: 35523-298/2013-13, dated 22.10.2013

VGP Maribor: Pesnica flood relief channel, project no.: 940/4-83, February 1983