## 2. SKLOP
Opis opreme | Description of equipment | cena/enoto EUR (brez DDV)
total price EUR (without tax)
2. SKLOP RASTLINJAKA | 2. SET OF GREENHOUSE
Rastlinjak kot celota je razdelejen na dva sklopa izvedbe, pri čemer je 1. sklop že izveden in je vseboval izvedbo zunanjega ovoja rastlinjaka (konstrukcija iz aluminija z zasteklitevijo s pripadajočimi vrati in sistem senčenja), 2. sklop, ki je predmet tega javnega naročila pa vključuje izvedbo notranjosti rastlinjaka vključno z regulacijo (predelne stene s pripadajočimi vrati, električne, strojne in vodovodne inštalacije, senzorji in regulacija klimatskih pogojev ter mize) | The greenhouse as a whole is divided into two sets of construction, where the 1st set that included the construction of the outer casing of the greenhouse (aluminum construction with glazing with associated doors and shading system) is already constructed; and the 2nd set that includes complete construction of the greenhouse interior including regulation (inner walls including doors, electrical, mechanical and plumbing installations, sensors and regulation of climatic conditions and tables) and is the subject of this public procurement.
Splošne zahteve za 2. sklop rastlinjaka: | General requiremens for the 2. set of greenhouse:
2. sklop rastlinjaka se izvede oz. montira na prej pripravljeno talno gradbeno osnovo in na izveden 1. sklop rastlinjaka. | 2. set of the greenhouse is constructed or mounted on a previously executed roof slab and a previously prepared 1. set of greenhouse.
Dobavitelj rastlinjaka mora detajle izvedbe uskladiti z odgovornim projektantom načrta arhitekture pred pričetkom izdelave načrta rastlinjaka. | The greenhouse supplier must coordinate the construction details with the architectural project leader before starting the production of the greenhouse plan.
Dobavitelj mora pri izdelavi rastlinjaka upoštevati: > največja dovoljena električna moč: 150 kW - 12,5 kW (za 5 rastnih komor reach-in, ki bodo nameščene v prostorih 02.07.02 in 02.07.10 znotraj rastlinjaka in niso predmet tega razpisa) = 137,5 kW (za 1. in 2. sklop rastlinjaka) > oddana toplota 5 rastnih komor reach-in tip FytoScope FS-RI SN: FS-RI-1600-009, od katerih bodo tri nameščene v prostoru 02.07.02 (skupna toplotna moč 1500 W) in in dve v prostoru 02.07.10 (skupna toplotna moč 1000 W) znotraj rastlinjaka in niso predmet tega razpisa > največja dovoljena moč naprav povezanih na diesel agregat in UPS: 3 fazna napetost 150kW-DEA, enofazna napetost 1kW-UPS > na razpolago je trifazni električni piključek električna moč 150kW, 400V 3F, ničla TN-C/S + zemlja, vezano na DEA 150kW in 1kW 230V AC na UPS. > komunikacijski protokolih povezave na CNS sistem stavbe, Modubus RTU > največje dovoljeno število telekomunikacijskih priključkov (univerzalno ožičenje): 5 > razpoložljivi mediji: - če bo uporabljen glikol, mora biti uporabljen glikol Petrol antifriz univerzal - če bo uporabljen hladilni plin, mora biti uporabljen hladilni plin R32, energetska učinkovitost naprave naj bo SCOP > 3 - razpoložljiva sanitarna voda (topla in hladna) na priključku v prostoru 02.07.02 s tlakom 3 bar, pretokom do 1000 litrov/uro in dimenzijo cevi DN20 - na razpolago je do 150 litrov demi vode s prevodnostjo manj kot 5 μS na dan (tlak 3 bar), v kolikor ponudnik potrebuje več demi vode ali mehko vodo z drugačno prevodnostjo, mora ponudnik zagotoviti napravo za mehčanje vode (vodovodna voda na lokaciji ima trdoto 13 - 15 °N (°d, °DH)) > .že predvidene lokacije in dimenzije talnih odtokov odpadne vode v komorah in predprostorih (točne lokacije odtokov kondenzne vode v posameznih komorah določi ponudnik) | The supplier must take into account when making the greenhouse: > maximum permissible electrical power: 150 kW - 12.5 kW (for 5 reach-in growth chambers, which will be installed in rooms 02.07.02 and 02.07.10 inside the greenhouse and are not the subject of this tender) = 137.5 kW (for the 1st and 2nd set of the greenhouse) > emitted heat of 5 reach-in growth chambers type FytoScope FS-RI SN: FS-RI-1600-009, three of which will be installed in room 02.07.02 (total heat power 1500 W) and two in room 02.07.10 (total thermal power 1000 W) inside the greenhouse and are not the subject of this tender > maximum permissible power of devices connected to the diesel generator or UPS: 150kW-DEA, 1kW-UPS > there is a 400V three-phase electric plug with electrical power 150kW, 400V 3F, neutral TN-C/S + ground, connected to DEA 150kW and 1kW 230V AC to UPS > communication protocols connecting to the building's CNS system, Modubus RTU > maximum permitted number of telecommunication connections (universal wiring): 5 > available media (technical gases, etc.) - if glycol is to be used, Petrol antifreeze universal glycol must be used - if refrigerant gas is to be used, refrigerant gas R32 or gas with SCOP above 3 must be used, the energy efficiency of the device should be SCOP > 3 - available sanitary water (hot and cold) at the connection in room 02.07.02: pressure 3 bar, flow rate up to 1000 liters/hour, pipe size DN20 - available up to 150 liters per day of demi water with electrical conductivity less than 5 mS (preasure 3 bar). If more demi water or soft water with different electrical conductivity is needed, the bidder must provide a water softener (tap water on site has a hardness of 13 - 15 °N (°d, °DH)) > already planned locations and dimensions of floor effluents in chambers and anterooms (exact locations of condensate drains in individual chambers are determined by the provider)
Dobavitelj rastlinjaka mora v ponudbi za izdelavo rastlinjaka prikazati podatke potrebnih medijev za delovanje rastlinjaka , upoštevajoč predhodno navedene razpoložljive moči na objektu, kot so: > hladilna in ogrevna moč v kWh, > potrebna električna moč v kWh, > podatke o potrebnih močeh naprav povezanih na diesel agregat oz. UPS, > podatke o komunikacijskih protokolih povezave na CNS sistem stavbe, > podatke o številu telekomunikacijskih priključkov (univerzalno ožičenje) ter > ev. podatke o drugih medijih (tehnični plini ipd.) | In the greenhouse bid, the greenhouse supplier must specify the requirements for the necessary media for the operation of the greenhouse, taking into account previously stated available power capacities of the building, such as: > cooling and heating power in kWh, > required electrical power in kWh, > data on the required power of devices connected to the diesel generator or. UPS > data on communication protocols for connection to the building's BMS system, > data on the number of telecommunication connections (universal wiring) and > data on other media (technical gases, etc.) if needed
Ponudba mora vključevati: > izdelavo delavniške dokumentacije (razen jeklene nosilne konstrukcije, aluminijaste konstrukcije, stekel in sistema senčanja, ki so predmet osnovnega projekta stavbe, s čimer je definirana končna oblika celote, oz. 1. sklopa rastlinjaka), ki ga mora pred izvedbo potrditi naročnik, > izvedbeni načrt strojnih instalacij (ogrevanje, hlajenje, prezračevanje z vlažanjem/sušenjem zraka, vodovod, odvajanje odpadne vode), > izvedbeni načrt električnih instalacij (splošna moč, razsvetljava), > ostalo potrebno dokumentacijo za izvedbo in delovanje rastlinjaka > dokumentacijo izvedenih del in vsa potrebna dokazila za izvedbio tehničnega pregleda in pridobitev uporabnega dovoljenja | The bid must include: > construction plan documentation (except for the load-bearing steel structure, aluminum structure with glazing and shading system, which are the subject of the basic design of the building, thus defining the final shape of the whole, or 1. set of greenhouse), which must be approved by the client before start of construction > construction plan of mechanical installations (heating, cooling, ventilation with humidification/air drying, plumbing and wastewater disposal) > construction plan of electrical installations (general power, lighting) > other necessary documentation for the implementation and operation of the greenhouse > documentation of all construction work and all evidences necessary for a successful technical inspection and obtaining an operating permit
Ponudba mora obsegati dobavo in montažo notranjosti rastlinjaka vključno s predelnimi stenami s pripadajočimi vrati, z mizami po specifikaciji in vsemi komponentami strojnih, električnih in vodovodnih napeljav, prezračevanja ter nadzornih sistemov vključno z napeljavami in končnimi distribucijskimi elementi (grelni in hladilni elementi, razsvetljava, cevi za zalivanje s šobami, senzorji ipd.). Ponudba mora obsegati vsaj en merilnik temperature, vlage in svetlobe (PAR) v vsaki komori. | The bid must include the supply and installation of the greenhouse interior, including inner walls with belonging doors, tables according to the specification; and all components of mechanical, electrical and plumbing installations, ventilation; and control systems including installations and final distribution elements (heating and cooling elements, lighting, water hoses with nozzles, sensors, etc.). The offer must include temperature, humidity and light (PAR) sensors at least one per chamber.
Ponudba mora vključevati dobavo in montažo: > centralnega nadzornega sistema (CNS) rastilnjaka in povezavo na CNS stavbe. Vgrajen CNS sistem v rastlinjaku mora omogočat nastavljanje parametrov delovanja in nadzora delovanja sistemov na daljavo (online). > senzoriko klimatskih in svetlobnih pogojev v rastlinjaku (regulacija umetne in naravne svetlobe), ki mora biti kompatibilna s sistemom senčenja, ki je izveden v okviru 1. sklopa rastlinjaka (tip, število in lokacija motorjev so razvidni iz prilog). Ponudnik mora zagotoviti tudi električne priključke motorjev senčil in avtomatiko. | The bid must include delivery and installation of: > building management system (BMS) of the greenhouse with a connection to the BMS of the building. The greenhouse BMS must enable remote (online) setting of operating parameters and control of the operation of system. > sensors of climatic and light conditions in the greenhouse (regulation of artificial and natural light), which has to be compatible with the shading system, built in the 1. set of greenhouse construction (type, number and location of motors can be seen from the attachments). The bidder must provide also electrical connections of the motors of the shading system and the automatisation.
Ponudnik mora zagotoviti ustrezen sisitem prisilnega prezračevanja rastnih komor ter prostorov 02.07.02 in 02.07.10. Za rastne komore mora ponudnik upoštevati: > vstopni zrak mora fltriran preko filtra G4 ali boljše > izhodni zrak mora biti filtriran preko filtra H10 ali boljše > pretok zraka mora biti vsaj 0,5x na uro > ne sme prihajati do mešanja zraka med posameznimi komorami > ne sme prihajati do mešanja vstopnega in izhodnega zraka | The provider must provide an adequate system of forced ventilation of the growth chambers and rooms 02.07.02 in 02.07.10. For growth chambers the provider must consider: > the intake air must be filtered through a G4filter or better filter > the outgoing air must be filtered through an H10 filter or better filter > the air flow must be at least 0,5x per hour > there must be no air mixing between the individual chambers > there must be no mixing of incoming and outgoing air
V tehnični etaži bodo priključki na dva tipa kanalizacij: - fekalno kanalizacijo in - onesnaženo kanalizacijo. Na fekalno kanalizacijo bosta priključena lijaka v 02.07.10 predprostoru in 02.07.02 sadilnici, ki nista predmet tega razpisa. Na onesnaženo kanalizacijo mora biti speljana vsa ostala odpadna voda iz notranjosti rastlinjaka. | The technical floor will have connections to two types of sewage systems: - faecal sewage system and - contaminated sewage system. To the faecal sewage system only the the two sink units in 02.07.10 anteroom and 02.07.10. planting room will be connected, which are not the subject of this tender All other wastewater from inside the greenhouse must be connected to contaminated sewage system.
Ponudnik mora eventualni kondenz in vso ostalo eventualno odpadno vodo od vseh strojnih strojnih naprav (npr. vlažilcev, razvlaževalcev, klim...) v vsaki komori speljati direktno na pripravljeno vertikalo onesnažene kanalizacije v prostora 02.07.10, ki se steka v jašek, kjer se vrši dekontaminacija onesnažene vode pred izlivom v javno kanalizacijo. | The bid must include the collection of all potential condensation water and any other potential waste water produced by any mechanical installation (e.g. humidifiers, dehumidifiers, fancoils...) in each chamber directly to the vertical of the contaminated sewage system in room 02.07.10, which runs through a shaft where decontamination of polluted water is carried out before it outpours into the public sewage system.
Korita miz v komorah naj nimajo odvoda odpadne vode. V rastlinjaku naj ne bo talnih sifonov. | Troughs of the tables in quarantine chambers should not have drainage of waste water. There should be no floor siphons in the greenhouse.
Ponudnik mora z izborom strojnih (hlajenje, ogrevanje, prezračevanje) in električnih naprav (razsvetljava), senzorike in CNS sistema zagotoviti fizikalne pogoje z dovoljenimi odstopanji skladno s spodaj navedenimi zahtevami za vsako komoro posebej. | By selecting mechanical (cooling, heating, ventilation) and electrical devices (lighting), sensors and BMS, the bidder must provide physical conditions in the greenhouse with permitted deviations in accordance with the below requirements for each chamber separately.
Vsaka komora v rastlinjaku mora pri delovanju omogočati in vsebovati: | In operation, each chamber in greenhouse must enable and contain:
> nastavljanje klimatskih pogojev in svetlobnih pogojev po vnaprej določenem časovnem zaporedju (urniku), dan/noč ipd. ločeno po posameznih rastnih komorah rastlinjaka | > setting of climatic and lighting conditions according to a predetermined time sequence (schedule), day / night, etc., separately in each chamber of the greenhouse
> programska oprema za nastavitev pogojev delovanja vsake komore z vsaj dvemi nivoji uporabnikov z vsaj eno licenco za vsak nivo | > software for settings of each camber conditions with at least two access levels with at least one license per level
> online merjenje parametrov (temperartura, jakost svetlobe, relativne vlažnosti) | > online measurement of parameters (temperature, light intensity, relative humidity)
> zbiranje podatkov v realnem času | > real-time data logging
> LCD prikazovalnik na dotik (min 10'') | > LCD touch screen (min 10 '')
> grafična predstavitev delovanja vsake komore (prikaz nastavljenih in trenutnih parametrov) | > graphical display of the operation of each chamber (display of set and current parameters)
> prenos podatkov preko Etherneta ali USB vmesnika | > data transfer via Ethernet or USB interface
> oddaljena kontrola delovanja preko LAN povezave | > remote operation control via LAN connection
> diagnostični sistem za spremljanje in beleženje napak pri delovanju vsake komore | > diagnostic system for monitoring and recording of each chamber malfunctions
Po končanju izvedbe rastlinjaka mora dobavitelj opraviti zagon rastlinjaka, preizkusiti delovanje ter nastaviti vse parametre delovanja rastlinjaka - vse skupaj s pooblaščenimi predstavniki naročnika - ter pripraviti poročilo o opravljenih meritvah in delovanju rastlinjaka. | After the completion of the greenhouse construction, the comissiong of the greenhouse, and testing of the operation and settings of all the parameters of the greenhouse should be performed - all together with the authorized representatives of the client - and prepare a report of the measurements and operation of the greenhouse.
Ponudba mora vključevati pripravo in predajo dokumentacije naročniku skladno s Pravilnikom o podrobnejši vsebini dokumentacije in obrazcih, povezanih z graditvijo objektov (Uradni list RS, št. 36/18, 51/18-popr. in 197/20). | The bid should include the preparation and submission of documentation to the client in accordance with the Rules on the detailed content of documentation and forms related to construction (Official Gazette of the Republic of Slovenia, No. 36/18, 51/18-.corr. and 197/20).
Ponudnik mora poskrbeti, da se v vsako komoro prestavi obstoječi javljalnik požara ali namesti nov ustrezen javljalnik požara (optični, termični,… javljalniki), povezan na požarno centralo objekta. Ponudnik mora zagotoviti vse potrebne podatke (količine in požarne lastnosti vgrajenih materialov) za dopnitev študije požarne varnosti. | The bidder must ensure that the existing fire detectors are reinstalled to each chamber or a new suitable fire detectors are installed (optical, thermal,... detectors). Fire detectors should be connected to the building's fire control system. The bidder must provide all the necessary data (quantities and fire properties of the installed materials) to supplement the fire safety study.
Garancijska doba in pogoji garancije ter odzivni čas za servis so določeni v splošnem delu razpisne dokumentacije. | The warranty period and warranty conditions, as well as the response time for service, are specified in the general conditions of the tender documentation.
Dobavitelj ob dobavi opreme dostavi naročniku delovna navodila ter izvede usposabljanje vsaj 6 uporabnikov, čas trajanja usposabljanja je najmanj 3 dni in učenje na daljavo dodatnih 60 ur. | Upon delivery of the equipment, the supplier also delivers work instructions to the client and conducts training for at least 6 users for the duration at least 3 days and with the additional 60 hours on-line.
Ponudnik mora zagotoviti generalni pregled pred potekom garancijske dobe ter po končanem pregledu izvesti meritve. V primeru odstopanja od specifikacij, odstope odpravi in preda ustrezno dokumentacijo. | The bidder should provide a general inspection before the expiration of the warranty period and perform measurements after the completion of the inspection. In case of deviation from the specifications deviations are corrected and the documentation is given to the client.
Izdelava in oprema rastlinjaka | Construction and equipment of the greenhouse
Notranja izdelava in oprema rastilnjaka zunanjih dimenzij 13,1 m x 20,2 m x 3,4 m na spodnjem robu in 5,2 m na zgornjem robu. Naklon strehe 7° (stopinj). Točne dimenzije ponudnik sam izmeri na lokaciji . | Interior construction and equipment of a greenhouse with external dimensions 13.1 m x 20.2 m x 3.4 m at the bottom edge and 5.2 m at the top edge. Roof pitch 7 ° (degrees). The bidder must measure the exact dimensions on the location.
Rastlinjak je tlorisno deljen na 3 predprostore, 2 predprostora komor ter 8 karantenskih komor, približne površine (A) in volumna (V) (točne dimenzije so pogojene z že izgrajenim zunanjim ovojem rastlinjaka): | The floor plan of the greenhouse is divided into 3 anterooms, 2 chamber anterooms and 8 quarantine chambers, of the approximate area (A) and volume (V) (the exact dimensions depend on the already existing outer casing of the greenhouse):
> 99.10.34 predprostor 1; A = 9,4 m2 | > 99.10.34 anteroom 1; A = 9,4 m2
> 02.07.10 predprostor 2; A = 9,7 m2 | > 02.07.10 anteroom 2; A = 9,7 m2
> 02.07.02 predprostor 3 (sadilnica); A = 9,3 m2 | > 02.07.02 anteroom 3 (sadilnica); A = 9,3 m2
> 02.07.01 predprostor komor 1; A = 7,2 m2; V = 35,0 m3 | > 02.07.01 chamber anteroom 1; A = 7,2 m2; V = 35,0 m3
> 02.07.15 predprostor komor 2; A = 7,2 m2; V = 32,0 m3 | > 02.07.15 chamber anteroom 2; A = 7,2 m2; V = 32,0 m3
> 02.07.03 karantenska komora 1; A = 43,9 m2; V = 193,7 m3 | > 02.07.03 quarantine chamber 1; A = 43,9 m2; V = 193,7 m3
> 02.07.07 karantenska komora 2; A = 33,2 m2; ; V = 171,5 m3 | > 02.07.07 quarantine chamber 2; A = 33,2 m2; ; V = 171,5 m3
> 02.07.08 karantenska komora 3; A = 10,8 m2; V = 56,0 m3 | > 02.07.08 quarantine chamber 3; A = 10,8 m2; V = 56,0 m3
> 02.07.09 karantenska komora 4; A = 14,7 m2; V = 74,6 m3 | > 02.07.09 quarantine chamber 4; A = 14,7 m2; V = 74,6 m3
> 02.07.11 karantenska komora 5; A = 18,5 m2; V = 91,8 m3 | > 02.07.11 quarantine chamber 5; A = 18,5 m2; V = 91,8 m3
> 02.07.12 karantenska komora 6; A = 17,9 m2; V = 89,3 m3 | > 02.07.12 quarantine chamber 6; A = 17,9 m2; V = 89,3 m3
> 02.07.13 karantenska komora 7; A = 10,5 m2; V = 43,3 m3 | > 02.07.13 quarantine chamber 7; A = 10,5 m2; V = 43,3 m3
> 02.07.14 karantenska komora 8; A = 10,4 m2; V = 43,2 m3 | > 02.07.14 quarantine chamber 8; A = 10,4 m2; V = 43,2 m3
skupna neto površina prostorov znotraj rastlinjaka: 202,7 m2 | total net area of rooms within the greenhouse: 202,7 m2
Konstrukcija notranjih predelnih sten z vrati mora izpolnjevati naslednje karakteristike: | The construction of inner walls including doors must meet the following requirements:
> aluminijasti in/ali vroče cinkani barvani jekleni profili bele barve Ponudnik mora zagotoviti dovolj toge stene, ki bodo preprečevale tresenje sten pri uporabi vrat. Stene morajo zagotavljalati ustrezno tesnost komor, pri čemer mora ponudnik zatesniti vse dilatacije med obstoječo jekleno in aluminijasto konstrukcijo zunanjega ovoja rastlinjaka z materialom, ki ni porozen, ima gladke površine in omogoča čiščenje. Pri tem mora ponudnik upoštevati podatek o zrakotesnosti zunanjega ovoja rastlinjaka iz priloge. Ustrezno togost je potrebno izkazati s statičnim izračunom, ki mora upoštevati horizontalno obremenitev 1kN. | > white AL profile and/or painted hot galvanized steel profile The bidder must provide walls rigid enough to prevent any vibrations while using doors. The walls must ensure adequate tightness of the chambers, whereby the bidder must seal all dilatations between the existing steel and aluminum construction of the outer casing of the greenhouse with a material that is not porous, has smooth surfaces and is suitable for cleaning.The bidder must consider the the air permeability of outer casing of the greenhouse given in the attachement. The appropriate rigidity of the walls must be proven with a static calculation, which must take into account the horizontal load 1kN.
> Za vse električne (vključno z lučmi), strojne in vodovodne inštalacije ter senzorje mora ponudnik zagotoviti lastno podkonstrukcijo sidrano na tla, razen če mu namestitev na obstoječo konstrukcijo odobri pooblaščeni statik naročnika. | > For all electrical (including lights), mechanical and plumbing installations and sensors, the provider must provide its own substructure, unless the installation on the existing structure is approved by the client's authorized structural engineer.
> zasteklitev z enojnim in dvoslojnim lepljenim varnostnim steklom VSG | > glazing with single and double-layered laminated safety glass VSG
> višina sten se mora prilagajati naklonu strehe (višina 3,4 m do 5,1 m) | > the height of the walls must be adjusted to the slope of the roof (height 3.4 m to 5.1 m)
> skupna površina notranjih steklenih sten približno 253,2 m2 (točne dimenzije so pogojene z že izgrajenim zunanjim ovojem rastlinjaka) | > total area of internal glass walls 253.2 m2 (the exact dimensions depend on the already existing outer casing of the greenhouse)
> skupno število enokrilnih notranjih vrat svetle širine dim. 80/210 cm: 9 kosov (6 levih + 3 desnih vratnih kril) | > total number of single-leaf interior doors of clear width dim. 80/210 cm: 9 pieces (6 left + 3 right door wings)
> skupno število dvokrilnih notranjih vrat svetle širine dim. 120/210 cm (primarno krilo 80 cm, sekundarno krilo 40 cm) z električno ključavnico in čitalnikom pristopne kontrole, ki je povezljiv s hišnim sistemom obstoječe pristopne kontrole (kot naprimer HID iCLASS SE R10): 2 kos | > total number of double-leaf interior doors of clear width dim. 120/210 cm (primary wing 80 cm, secondary wing 40 cm) with electric lock and access control reader that can be connected to the existing access control system of the building (such as HID iCLASS SE R10): 2 pcs
Predprostori | Anterooms
V predprostorih 99.10.34, 02.07.10 in 02.07.02 mora ponudnik zagotoviti prezračevanje, ogrevanje/hlajenje in splošna razsvetljava prostorov. | In the anterooms 99.10.34, 02.07.10, and 02.07.02, the provider must provide ventilation, heating/cooling and general lighting.
Mize | Tables
Podnožja miz morajo biti izdelana iz vroče galvaniziranih jeklenih profilov ali drugega ustreznega nerjavečega materiala. Podnožja mize morajo biti visoka 70 cm do 80 cm. | The bases of the tables must be made of hot-dip galvanized steel profiles or aluminium or another suitable stainless material. The bases of the tables should be 70 cm to 80 cm high.
Notranji deli korit morajo biti izdelana iz nerjavečega jekla v kvaliteti AISI 304 ali AISI 316L, finalna obdelava: fino brušeno; brez ostrih robov, vsi stiki varjeni in fino prebrušeni. Robovi korit morajo biti višine od 3 cm do 12 cm. | Inner part of troughs must be made of stainless steel in AISI 304 or AISI 316L quality, final treatment: finely ground; no sharp edges, all joints welded and finely ground. Sides of the troughs should be from 3 cm to 12 cm high.
Korita morajo biti vodotesna in morajo imeti ravno dno. | The troughs must be waterproof with flat bottom.
Za zalivanje mora biti v vsaki komori nameščena zalivalna cev z zalivalno šobo, ki omogoča doseg do vseh rastlin v komori. Zalivalne šobe morajo omogočati zalivanje brez škropljenja. | For watering, a watering hose with a watering nozzle must be installed in each chamber to allow access to all plants in the chamber. Watering nozzles should enable watering without spraying.
Mize se morajo dimenzijsko čim bolj ujemati s priloženimi izrisi glede na dimenzije že izgrajenega zunanjega ovoja rastlinjaka, razen tam, kjer zaradi stojnih inštalacij to ni možno. Mize morajo dimenzijsko ustrezati posamezni komori tako, da je prostor maksimalno izkoriščen. Globina miz mora biti 80 cm do 90 cm. Skupna površina vseh miz v rastlinjaku mora biti med 85 m2 in 100 m2. Prehodi med mizami morajo biti široki vsaj 80 cm. | The tables must match the dimensions of the attached drawings as closely as possible with respect to the dimensions of the already constructed outer casing of the greenhouse, except where this is not possible due to mechenical installations. The tables must fit the dimensions of each chamber so that the space is used to the maximum. The depth of the tables should be 80 cm to 90 cm. The total area of all the tables in the greenhouse must be between 85 m2 and 100 m2. Pathway between tables should be at least 80 cm.
Opis pogojev KARANTENSKIH KOMOR | Description of the conditions of QUARANTINE CHAMBERS
Približne dimenzije posameznih komor so razvidne iz priloženega izrisa. Dimenzije posameznih komor je potrebno prilagoditi dejanskim izmeram lupine rastlinjaka (izdelane v okviru 1. sklopa rastlinjaka). Dimenzije miz je potrebno prilagoditi dejanskim izmeram posameznih komor tako, da je prostor maksimalno izkoriščen. | The approximate dimensions of the individual chambers are given in the attached drawing.The dimensions of the individual chambers must be adjusted to the actual measurements of the outer casing of the greenhouse (constructed in the 1. set of the greenhouse). The dimensions of the tables must be adjusted to the actual measurments of the individual chambers in order of maximal usage of the available space.
> v vsaki komori 4x vtičnica 230 V, IP 44 | > in each chamber 4x socket 230 V, IP 44
> ustrezna stabilnost oz. homogenost temperature in vlage znotraj komore mora biti dosežena v 6 urah po nastavitvi parametrov režima (večinoma bodo posamezni poskusi potekali nekaj tednov pri konstantnih pogojih, ki pa se bodo razlikovali podnevi in ponoči: različni dnevni in nočni režim). | > appropriate stability and/or homogeneity of temperature and humidity inside the chamber must be achieved within 6 hours after setting the parameters of the regime (in most cases, individual experiments will take place for several weeks under constant conditions, but they will differ during the day and at night: different day and night regimes).
Tlak | Air pressure
> zračni pritisk: normalen v komorah 1, 2, 3, 5, 6, 7 in 8; podtlak 20 Pa v komori 4 | > air pressure: normal in chambers 1, 2, 3, 5, 6, 7 and 8; depression 20 Pa in chamber 4
Temperatura | Temperature
> dnevna temperatura v komorah 1, 2, 3, 4, 5, 7 in 8 mora biti nastavljiva v korakih po 1°C v temperaturnem območju med 21°C in 28°C. | > the daily temperature in chambers 1, 2, 3, 4, 5, 7 and 8 must be setable in steps of 1°C in the temperature range between 21°C and 28°C.
> nočna temperatura v komorah 1, 2, 3, 4, 5, 7 in 8 mora biti nastavljiva v korakih po 1°C v temperaturnem območju med 18°C in 25°C. | > the night temperature in chambers 1, 2, 3, 4, 5, 7 and 8 must be setable in steps of 1°C in the temperature range between 18°C and 25°C.
> dnevna temperatura v komori 6 mora biti nastavljiva v korakih po 1°C v temperaturnem območju med 21°C in 28°C, v zimskem času pa v korakih po 1°C temperaturnem območju med 4°C in 28°C. | > the daytime temperature in chamber 6 must be setable in steps of 1°C in the temperature range between 21°C and 28°C, and in winter in steps of 1°C in the temperature range between 4°C and 28°C.
> nočna temperatura v komori 6 mora biti nastavljiva v korakih po 1°C v temperaturnem območju med 18°C in 25°C, v zimskem času pa v korakih po 1°C temperaturnem območju med 4°C in 25°C. | > the night temperature in chamber 6 must be setable in steps of 1°C in the temperature range between 18°C and 25°C, and in winter in steps of 1°C in the temperature range between 4°C and 25°C.
> temperaturna stabilnost v komorah: dejanska temperatura v komori ne sme odstopati več kot 3°C od nastavljene temperature, razen: - v poletnem času, ko je zunanja temperatura okolja več kot 12°C višja od nastavljene temperature - v tem primeru mora biti temperatura v komori vsaj 12°C nižja kot je zunanja temperatura okolja. - v zimskem času v komori 6, ko je zunanja temperatura višja od nastavljene temperature - v tem primeru temperatura v komori ne sme biti višja kot je zunanja temperatura okolja. | > temperature stability in chambers: the actual temperature in the chamber must not deviate by more than 3°C from the set temperature, except: - in summer, when the outside temperature of the environment is more than 12°C higher than the set temperature - in this case the temperature in the chamber must be at least 12 °C lower than the outside ambient temperature. - in winter in chamber 6, when the outsite temperature of the environment is higher than the set temperature - in this case, the temperature in the chamber must not be higher than the outside temperature of the environment..
> temperaturna homogenost znotraj komore: znotraj komore mora biti dosežena temperaturna homogenost 4°C, kar pomeni, da se na različnih pozicijah znotraj komore temperatura ne sme razlikovati za več kot 4°C. | > temperature homogeneity inside the chamber: temperature homogeneity of 4°C must be achieved inside the chamber, which means that the temperature must not differ by more than 4°C in different positions inside the chamber.
Vlažnost | Humidity
> vlažnost: vlažnost mora biti nastavljiva v korakih po 5% v območju med 50% in vsaj 75% relativne zračne vlage. | > humidity: the humidity must be setable in steps of 5% in the range between 50% and at least 75% relative humidity.
> stabilnost vlažnosti: dejanska vlaga v komori ne sme odstopati več kot 10% od nastavljene vlage | > humidity stability: the actual humidity in the chamber must not deviate by more than 10% from the set humidity
Osvetlitev | Illumination
> jakost osvetlitve (PPFD): najmanj 200 umol/m²s na vsaj 90% površine miz v temi ob prižganih lučeh. Ta jakost osvetlitve mora biti dosežena, kadar so luči nameščene ne nižje kot 50 cm nad mizo. | > illumination (PPFD): minimum 200 umol/m²s at al least 90% of the surface of the tables (lights on, dark outside). This illumination must be achieved when the lights are positioned not lower than 50 cm from the table.
> homogenost osvetlitve znotraj komore: v temi ob prižganih lučeh se na različnih mizah v isti komori in na različnih pozicijah na mizi osvetlitev ne sme razlikovati za več kot 100 umol/m²s. | > homogeneity of illumination inside the chamber: in the dark with the lights on, the illumination must not vary by more than 100 umol/m²s on different tables in the same chamber and at different positions on the table.
> valovna dolžine osvetlitve (K): LED osvetlitev, bela svetloba celotnega spektra (čim bolj podobna sončni svetlobi) | > illumination wavelength (K): LED illumination, full spectrum white lights (as similar to the sun light as possible)
> Luči morajo biti nastavljive po višini najmanj od 50 cm do vsaj 150 cm nad mizo v komorah 1, 7 in 8, v komorah 2, 3, 4, 5 in 6 pa od 50 cm do vsaj 200 cm nad mizo. | > Lights must be height adjustable at least from 50 cm to at least 150 cm above the table in chambers 1, 7 and 8, and in chambers 2, 3, 4, 5 and 6 from 50 cm to at least 200 cm above the table.
Skupaj brez DDV | TOTAL WITHOUT TAX
DDV | TAX | 0
Skupaj z DDV | TOTAL WITH TAX | 0