Naziv projekta: Nadgradnja nacionalnih raziskovalnih infrastruktur – RIUM

Project title: Upgrading National Research Infrastructures – RIUM

Tehnične specifikacije za modularni čisti prostor

Technical specifications for a modular clean room

- PREDMET JAVNEGA NAROČILA 						1. SUBJECT OF THE PUBLIC TENDER

| Predmet javnega naročila je nabava modularnega čistega prostora, vključno z dobavo, vnosom, namestitvijo, montažo, konfiguracijo, inštalacijo in zagonom filtrnih enot za ventilacijski sistem ter meritvami, skladno s tehničnimi specifikacijami. Lokacija dobave in vnos opreme: Univerza v Mariboru, Fakulteta za elektrotehniko, računalništvo in informatiko, Koroška cesta 46, 2000 Maribor, Slovenija, Laboratorij za elektro-optične in senzorske sisteme objekt G, prostor G-127, skladno s prilogo 1 teh specifikacij, kjer je podan tloris prostora, kamor bo izbrani ponudnik moral modularni čisti prostor vnesti in namestiti. Naročnik bo ponudnikom omogočil ogled prostora na lokaciji vnosa in namestitve opreme, skladno s točko 11.2.7 Navodil ponudnikom. Rok dobave: do 15.3.2023 Garancijski rok: najmanj 1 (eno) leto od dneva podpisa prevzemnega zapisnika. Dobavitelj mora v času garancijskega roka zagotavljati brezplačna garancijska popravila in oskrbo z rezervnimi deli. Ponudnik mora zagotoviti da: - modularni čisti prostor ustreza zahtevani klasifikaciji delcev na 1 m3 zraka po standardu ISO 14644-1:2015, - ustrezen nadtlak čistega zraka, ki preprečuje vdor umazanega zraka iz okolice v notranjost modularne čiste sobe, - da so električne instalacije, osvetlitev in računalniške povezave v modularnem čistem prostoru izvedene glede na minimalne tehnične zahteve, opisane v spodnji tabeli, - da so tlaki v modularnem čistem prostoru izvedeni tako, da ustrezajo zahtevanemu ISO standardu, ki velja za čiste prostore. V ceno so vključena tudi uporabniška navodila za pravilno uporabo modularnega čistega prostora. Usposabljanje ni potrebno. V ponudbi mora biti zajeti ves droben material, ki je potreben za namestitev čistega prostora, tudi če ni izrecno naveden. | Subject of the public tender is a modular clean room, with delivery placement, assembly, configuration, installation of the fan filter units with compliance test, in line with technical specifications. Equipment delivery and placement: University of Maribor, Faculty of Electrical Engineering and Computer Science, Laboratory for Electro-Optics and Sensor Systems, Koroška cesta 46, 2000 Maribor, Slovenia, Building G, G-127, in line with Annex 1 to these specifications and providing the floor plan of the laboratory, where the modular clean room shall be delivered and mounted by the successful tenderer. The contracting authority will enable the tenderers to inspect the laboratory on site in line with Point 11.2.7 of the Instructions to tenderers. Delivery time: until 15 March 2023 The warranty period: At least 1 (one) year from the day of signature of the take-over protocol. During the warranty period, the Supplier has to provide free warranty repairs and spare parts supply The tenderer must ensure that: - the modular clean room specifications correspond to the required classification of particles per 1 m3 of air according to ISO 14644-1: 2015, - adequate clean air overpressure to prevent the ingress of unclean air from the surroundings into the interior of the modular clean room, - the electrical installations, lighting and computer network connections in the modular clean room are carried out in accordance with the minimum technical requirements described in the table below, - the flooring in the modular clean room is designed to comply with the required ISO standard applicable to clean rooms. The price also includes user instructions for use of the modular clean room. Training is not necessary. The offer must include all the small material needed to install the modular clean room, even if it is not explicitly stated. |
| --- | --- |

TEHNIČNE ZAHTEVE

- TECHNICAL SPECIFICATIONS

| Modularni čisti prostor Univerza v Mariboru naroča modularni čisti prostor, katerega je mogoče umestiti v obstoječ prostor na naslovu uporabnika. Čisti prostor je sestavljen iz enega prostora v katerem je predvidena stropna distribucija HEPA filtriranega zraka, količinsko prilagojena zagotavljanju ustreznega kaskadnega tlaka proti okolici. Zadostna količina in ustrezna filtracija zraka mora zagotavljati čistost znotraj prostora v zahtevani stopnji po ISO standardu. Krmiljenje čistega prostora mora zagotavljati tudi ustrezno alarmiranje v primeru zamašenosti filtrov. Modularni čisti prostor mora imeti ustrezno osvetlitev izvedeno s primernimi osvetlitvenimi telesi ter z zastekljenimi predelnimi stenami modularnega čistega prostora. Elektro inštalacije morajo biti izvede tako, da tudi omogočajo priklop porabnikov z večjimi nazivnimi močmi, katere so navedene v minimalnih tehničnih zahtevah. Tlaki v modularnem čistem prostoru morajo biti izvedeni v antistatični izvedbi z ustreznim odvajanjem statične elektrine. V nadaljevanju so podane minimalne tehnične zahteve. Ponudba mora izpolnjevati ali presegati vse minimalne tehnične zahteve. | Thin modular clean room The University of Maribor is purchasing a modular clean room, which can be set in an existing room at the client's facilities. The modular clean room consists of one room in which the ceiling distribution of HEPA filtered air is planned, quantitatively adjusted to ensure adequate cascade pressure towards the surroundings. According to the ISO standard, an adequate air filtration must ensure cleanliness inside the room to the required degree. Clean room control must also provide an adequate alarm in the event of filter clogging. The modular clean room must have adequate lighting with suitable lighting fixtures and glazed panel of the modular clean room. Electrical installations must be carried out so that they also enable the connection of high-rate power equipment, which is specified in the minimum technical requirements. The flooring in the modular clean room must have an antistatic design with adequate design for the discharge of static electricity. Minimum technical requirements are given below. The offer must match or exceed all minimum technical requirements. |
| --- | --- |

| Številka postavke Item No. | Število kosov No. of pieces | ZAHTEVANO | REQUIRED |
| --- | --- | --- | --- |
| 1 | 1 | Minimalne tehnične zahteve: Dimenzije čistega prostora: - Notranje dimenzije: dolžina ≥ 5000 mm; širina ≥ 4000 mm; višina ≥ 2500 mm - Zunanje dimenzije: višina ≤ 3000 mm Predelne stene modularnega čistega prostora: - Material: Aluminij (Al) - Zaključni sloj: prašno barvan - Debelina predelne stene: ≥ 45 mm - Zasteklitev izvedena v vsaj dveh stenah - Dimenzije stekla: višina: ≥ 1200 mm; širina ≥ 1200 mm - Zasteklitev izvedena z dvojno zasteklitvijo ali s kaljenim steklom - Barva zaključnega sloja: RAL 9010 Vrata za modularni čisti prostor: - Širina vratnega krila: ≥ 1000 mm - Višina vratnega krila: ≥ 2000 mm - Debelina vratnega krila: ≥ 45 mm - Zastekljeno vratno krilo z dimenzijami stekla: višina: ≥ 700 mm; širina ≥ 500 mm - Zasteklitev izvedena z dvojno zasteklitvijo ali s kaljenim steklom - Vgrajeno talno tesnilo. - Magnetno zapiranje vratnega krila brez dodatnih gumi tesnil. - Možnost hitre montaže in demontaže vratnega krila. - Omogočeno odpiranje vratnega krila do 180 stopinj - Barva zaključnega sloja: RAL 9010 Filtrirni sistem: - Sistem, ki omogoča stopnjo čistosti prostora vsaj 7 po ISO standardu 14644-1:2015. - Ročno ali avtomatsko krmiljen sistem prezračevanja. - Glasnost filtrirne enote: ≤ 70 dB - Filtri: vsaj 14 HEPA in G4 pred filter - Merilnik diferenčnega tlaka Tlaki: - Antistatični epoksi tlak. - Odvajanje statične elektrine izvedeno z ozemljitvijo Elektro inštalacije, osvetlitev in računalniško omrežje: - Parapetni kanal z minimalno 6 vtičnicami. - Vsaj 2 vtičnici morata omogočati priključitev porabnikov z nazivnimi močmi: ≥ 5000 W - Priključek za povezavo z računalniškim omrežjem: ≥ 2 priključka - Stropne LED luči - Priključitev modularnega čistega prostora na električno in računalniško omrežje mora biti izvedena preko obstoječe infrastrukture, ki se nahaja v laboratoriju | Minimum technical requirements: Modular clean room dimensions: - Inner dimensions: length minimal 5000 mm; width minimal 4000 mm; height minimal 2500 mm - Outer dimensions: height maximum 3000 mm Partition walls of the modular clean room: - Material: Aluminum (ALU) - Final layer: powder coated - Thickness: minimal 45 mm - Glazing of minimal two (2) partition walls. - Glazing dimensions: height minimal 1200 mm; width minimal 1200 mm - Double glazed or tempered glass - Final layer color: RAL 9010 Modular clean room door: - Door leaf width: minimal 1000 mm - Door leaf height: minimal 2000 mm - Door leaf thickness: minimal 45 mm - Glazed door leaf with the following glass dimensions: height minimal: 700 mm; width minimal 500 mm - Double glazed or tempered glass - Door leaf with built in floor seal - Magnet door closing without additional rubber seals - Possibility of quick assembly and disassembly of the door leaf - Enabled door leaf opening up to 180 degrees - Final layer color: RAL 9010 Filtering system: - Minimal ISO 7 class (according to the 14644-1:2015 standard) filtering system - Manual or automatic controlling venting system - Fan filtering unit (FFU) noise: maximum 70 dB - Filters: minimal 14 HEPA and G4 pre-filter - Differential Pressure Gauge Flooring: - Antistatic epoxy floor - Antistatic design with adequate static electricity discharge design electricity by earthing Electrical installations, lighting and computer network: - Parapet trunk with minimal six (6) sockets - Minimal two (2) sockets must be compatible with high power devices, minimal 5000 W - Minimal two (2) ethernet sockets - Ceiling lightning with LED light - Connecting a modular clean room to an electrical and computer network must be carried out through an existing infrastructure located in the laboratory |

Priloga 1: Tloris prostora G-127 in predvidena umestitev modularnega čistega prostora

Annex 1: Floor plan of room G-105 with and planned installation location of the modular clean room

Operacijo sofinancirata Republika Slovenija, Ministrstvo za izobraževanje, znanost in šport in Evropska unija iz Evropskega sklada za regionalni razvoj. Operacija se izvaja v okviru Operativnega programa za izvajanje evropske kohezijske politike 2014-2020 v okviru prednostne osi 1: »Mednarodna konkurenčnost raziskav, inovacij in tehnološkega razvoja v skladu s pametno specializacijo za večjo konkurenčnost in ozelenitev gospodarstva«, prednostne naložbe 1.1 »Krepitev infrastrukture za raziskave in inovacije ter zmogljivosti za razvoj odličnosti na tem področju, pa tudi spodbujanje pristojnih centrov, zlasti takšnih, ki so evropskega pomena«, specifičnega cilja 1.1.1 »Učinkovita uporaba raziskovalne infrastrukture ter razvoj znanja/kompetenc za boljše nacionalno in mednarodno sodelovanje v trikotniku znanja«.

The operation is co-financed by the Republic of Slovenia, Ministry of Education, Science and Sport and the European Union from the European Regional Development Fund. The operation is carried out under priority axis 1: ''International competitiveness of research, innovation and technological development, in line with smart specialization for increased competitiveness and greening of the economy'', priority investment 1.1 ''Strengthening R&D infrastructure and capacity to develop excellence in this and the promotion of competent centers, especially those of European importance'', specific objective 1.1.1 ''Efficient use of research infrastructure and development of knowledge / competences for better national and international cooperation in the knowledge triangle'' under the Operational Program for implementation of the European cohesion policy 2014-2020.