Ref. No.: 285-15/4-2022

Date: 27. 12. 2022

TECHNICAL SPECIFICATION AND REQUIREMENTS FOR THE “VOIP VCS SYSTEM” Corr version 1

© 2022 Slovenia Control. All rights reserved. No part of this document may be reproduced, transmitted, stored in a retrieval system or translated into any language, in any form, or by any means, without the prior written consent of Slovenia Control.

Intentionally Left Blank

Table of Contents

1	Introduction	7

1.1	Purpose	7

1.2	Scope	7

1.3	General	7

1.4	Reference Documents	8

1.4.1	Standards	8

1.4.2	Regulatory Documents	8

1.5	Definitions	9

1.6	Abbreviations	9

2	System Architecture	12

2.1	System Structure	12

2.2	System Restart	14

2.3	System Software	15

2.4	System capacity	15

2.4.1	Operator Working Positions	16

2.4.2	Audio devices	16

2.4.3	Interfaces	17

2.4.4	TMCS	19

3	System Deployment	20

3.1	Structure and redundancy of the system	22

3.2	Structure and Redundancy of external connectivity	23

3.3	Robustness and Behaviour	24

4	Voice Communication System	26

4.1	General	26

4.2	Legacy Interfaces	27

4.3	Communication Types	28

4.4	Audio Quality	28

4.4.1	Noise	28

4.4.2	Distortion	29

4.5	Telephone and Intercom Services, Functions and Features	29

4.5.1	General	29

4.5.2	Direct access (DA)	30

4.5.2.1	Outgoing calls	31

4.5.2.2	Incoming calls	31

4.5.3	Indirect access (IA)	33

4.5.3.1	Outgoing calls	33

4.5.3.2	Incoming calls	33

4.5.4	Call timeout	34

4.5.5	Redial	34

4.5.6	Numbering scheme	34

4.5.7	Hotline	35

4.5.8	Priority	36

4.5.9	Transfer (Call forwarding)	36

4.5.10	Hold	37

4.5.11	Conference	37

4.5.12	Call pickup	38

4.5.13	Call divert	39

4.5.14	Parallel signaling	40

4.5.15	Position monitoring	40

4.5.16	Telephone book	40

4.5.17	End key	41

4.5.18	Call reporting	41

4.6	Radio Services, Functions and Features	41

4.6.1	General	42

4.6.2	Frequency selection	44

4.6.3	Receive mode	45

4.6.4	Receive indication	46

4.6.5	Transmit mode	47

4.6.6	Transmit configuration	48

4.6.6.1	Transmitter selection mode	48

4.6.6.2	Multi-station carrier mode (CLIMAX)	49

4.6.7	Coupling	49

4.6.8	Best signal selection	50

4.6.8.1	Site transmitter follows BSS	51

4.6.8.2	Site transmitter selected by the operator	52

4.6.9	Sidetone	52

4.7	TMCS	52

4.7.1	General	52

4.7.2	System configuration	54

4.7.2.1	General	54

4.7.2.2	Global configuration	54

4.7.2.3	Position configuration	55

4.7.3	Monitoring functions	56

4.7.3.1	Current status	56

4.7.3.2	History file	56

4.7.3.3	Diagnostics	57

4.7.3.4	Alarm file	58

4.7.4	Statistics	58

4.7.5	SNMP output	59

4.8	Roles, Missions and Re-configuration of Sectorization	60

4.8.1	Roles	60

4.8.2	Missions	61

4.8.3	Functional Requirements	62

4.9	Operator Working Position	62

4.9.1	Operator panel	63

4.9.2	Panel layout	65

4.9.3	User devices	65

4.9.3.1	Handset	66

4.9.3.2	Loudspeaker	66

4.9.3.3	Microphone	66

4.9.4	Volume control	67

4.9.5	Audio routing and device selection	68

4.9.6	Sockets	68

4.9.7	Split headset	69

4.9.7.1	Audio Routing	69

4.9.7.2	Audio Control	70

4.9.8	Audio indication	70

4.9.9	Panel controls	71

4.9.9.1	Brightness control	71

4.9.9.2	Chime	71

4.9.9.3	Cleaning mode	72

4.9.10	Training on operator working position	72

4.9.11	HMI design and interaction	72

4.9.12	Short Term Recording	73

4.9.13	Position unattended	74

4.10	Legal recording	74

4.11	Interface Specifications	75

4.11.1	General	75

4.11.2	Network capabilities – open standard interconnection	76

4.11.3	Telephone interfaces	76

4.11.3.1	General	76

4.11.3.2	Audible tones	77

4.11.3.2.1	Ring-back tone	77

4.11.3.2.2	Interrupt warning tone	77

4.11.3.2.3	Terminal busy tone	78

4.11.3.2.4	Unserviceable tone	78

4.11.3.3	Interface types	79

4.11.3.3.1	FXS interface	79

4.11.3.3.2	PSTN and PABX line interface	79

4.11.3.3.3	MFC line interface	79

4.11.3.3.4	QSIG line interface	80

4.11.3.3.5	Primary ISDN line interface	80

4.11.3.3.6	ATS-SIP VoIP interface	80

4.11.4	Radio interfaces	82

4.11.4.1	General	82

4.11.4.2	Interface types	82

4.11.4.2.1	4-wire	82

4.11.4.2.2	VoIP interface	82

4.11.5	3rd party systems interfaces (external systems)	82

4.12	Transit	84

4.13	System timing	84

4.14	RAM (Reliability, Availability, Maintainability)	85

4.14.1	General	85

4.14.2	Reliability	85

4.14.3	Maintainability	86

4.14.4	Availability	87

4.15	Network Requirements	87

4.16	Interoperability	88

5	VCS – System Integration Platform	89

5.1	General	89

5.2	Multiple Site Operation	89

5.3	Monitoring	90

5.4	Security & Safety	90

5.5	IT Security	91

5.6	System Design	91

5.7	Test and Deployment system – Testbed	92

6	Logistic Support	92

6.1	Maintenance Concept	92

6.2	Spares and Support	93

6.2.1	General	93

6.2.2	Mandatory Spare Parts List	94

6.2.3	Recommended spare parts	94

6.3	Warranty	94

6.3.1	General	94

6.3.2	Warranty Period	95

6.3.3	Obligations of the Contractor	95

7	Technical System Documentation	97

8	Training	99

9	Safety, Quality and Security Assurance	102

9.1	Safety	102

9.1.1	General	102

9.1.2	Safety Audit	103

9.1.3	Safety Plan	103

9.1.4	Safety Reports	103

9.1.5	Software Safety Requirements	104

9.2	Quality	106

9.2.1	General	106

9.2.2	Quality Assurance Plan	106

9.2.3	Quality Audit	107

9.3	Security	107

9.3.1	General	107

9.3.2	System Hardening (w.r.t. cyber security)	109

9.3.3	Security Training	109

9.3.4	Security Recomendations	109

10	Project Management	110

10.1	General	110

10.2	Project Management Plan	111

10.3	Documentation Plan	112

10.4	Logistic Support Plan	112

10.5	Installation and Commissioning Plan	113

10.6	Acceptance Test Plans and Procedures	113

11	Installation and Commissioning/Transition	114

11.1	Installation	114

11.1.1	Racks	115

11.1.2	Environmental conditions	116

11.1.2.1	Environmental operational conditions	116

11.1.2.2	Environmental storage conditions	116

11.1.3	Power supply	116

11.2	Pre-Commissioning and Completion	117

11.3	Commissioning and Transition	117

12	Verification Requirements	118

12.1	Test documentation	118

12.2	System Test	118

12.3	Factory Acceptance Test	118

12.4	Site Acceptance Test	119

# Introduction

## Purpose

Slovenia Control Ltd. (referred also as: the Contracting authority) is an air navigation service provider (ANSP) which provides – among other services – voice communication between controllers and pilots as well as with other ATS adjacent units.

In order to fulfil a safe and reliable A/G and G/G communication service, Slovenia Control Ltd. intends to purchase a new VCS to replace the existing VCS equipment at the sites ATCC and Airports Brnik, Portorož and Maribor. The replace of existing VCS equipment is intended for:

- Better reliability – the existing equipment is at the end of the life cycle;

- Improving functionality at Airports Portorož and Maribor;

- Easier and modern connectivity with adjacent centres;

- Future smooth and easy migration from TDM to VoIP technology.

In the following technical clauses the technical and operational requirements for the new system are described.

## Scope

The new VCS shall consist of two systems/components:

- Operational system for ATCC and Airports Brnik, Portorož and Maribor;

- Training system for Simulator and Test system;

Both systems/components shall include OWP subsystem and Technical Monitoring and Control (TMCS) subsystem.

## General

GERQ0010	The submitted tender documentation together with submitted technical documentation shall be neatly sorted in adequate sections and bound.

GERQ0020	The response to the specification is required to be comprehensive with a completed Compliance table as set out below.

GERQ0030	Tenderers are encouraged to offer the existing baseline products that are compliant with or equivalent to all mandatory requirements.

GERQ0040	The offered system shall have at least the same or better technical characteristics as requested in this tender.

GERQ0050	The Compliance table included in each chapter of this document provides an entry for each requirement.

The Tenderer shall also provide additional remarks if they are considered helpful for assessing the response. Each remark shall be uniquely referred to corresponding document (Chapter, Paragraph).

GERQ0060	The Tenderer compliance status shall be indicated against each paragraph of this specification in the ’Compliance’ column with a Yes for Compliance or a No for Non-Compliance. No other response shall be recognised during the evaluation and absence of Yes or No shall be counted as Not Compliant.

GERQ0070	The Tenderer shall provide the proof/explanation of every indicated Yes – Compliance in the ’Compliance’ column. Additionally, where the answer can be found in the submitted documentation, the Tenderer shall provide the reference and point to the specific line/paragraph/chapter/document where the compliance status can be verified.

GERQ0080	The Tenderer shall state references of already installed VoIP Voice Communication Systems for Air Traffic Control Centres/countries, members of Eurocontrol. The technical capacity of the Tenderer shall be proved by submitting the following documents/information:

- The Tenderer/Supplier/Manufacturer shall prove that the offered system has been installed and accepted (SAT signed) in at least three (3) reference projects in Eurocontrol area, demonstrating his experience in supplying full VoIP VCS (no hybrid systems) according to ED-137B/C in an ATM environment, with size and complexity similar to Slovenia Control’s system.

- The bidder shall present three (3) references of the VCS system/equipment. This means that according to the requirement: “VoIP VCS (no hybrid systems) according to ED-137B/C in an ATM environment, with size and complexity similar to Slovenia Control’s system” the references shall be for system or equipment, supplied to buyers in the Eurocontrol area, such a reference can be issued by the system/equipment manufacturer or supplier or end-user of such system/equipment. In case equipment manufacturer or supplier references are presented the buyer reserves the right to check the references at the final end-user of the system/equipment.

Note: By “no hybrid systems” it is understood that the connection of the IP VCS communication core to the IP capable resources (IP telephony lines and IP radios) is realized without the need of additional gateways/protocol converters that adapt the voice signals from analogue/TDM to VoIP.

- The Tenderer/Supplier/Manufacturer shall prove that he has successfully installed in at least one reference project interfaces that enable the full VoIP VCS to address analogue radios located at a remote site over an IP-based WAN.

- The bidder shall present one (1) reference for a comparable VCS system implementation, comparable to the one offered based on the buyer’s specifications. Implementation of a comparable VCS system is considered if the bidder’s reference project includes successfully installation of interfaces that allow full VoIP VCS for remotely installed analogue radio receiver addressing using remote WAN over IP. Such a technical capability can be provided by the system/equipment manufacturer or supplier or end-user of such system/equipment. In case equipment manufacturer or supplier references are presented the buyer reserves the right to check the references at the final end-user of the system/equipment.

GERQ0084	Slovenia Control reserves its right to visit and assess the user expierence for the references the Tenderer indicated.

GERQ0090	For all standards, certificates and regulations requested herein, the Contractor and all named subcontractors, or in case of a consortium all consortium members, shall comply with the respective requirement.

## Reference Documents

Wherever reference is made in this technical specification to specific regulations, standards and codes, the provisions of the latest current edition or revision of the relevant regulations, standards or codes in effect shall apply unless otherwise expressly stated in the technical specifications. Where such standards and codes are national or related to a particular country or region, other authoritative standards that ensure substantial equivalence to the standards and codes specified will be acceptable.

### Standards

RDST0010	The system design of the proposed VCS and whole supplied equipment shall work completely in Compliance with the following documents:

ICAO standards / recommendations

- ICAO Annex 10 (where applicable)

- ICAO Annex 11 (where applicable)

ED-136 – VoIP ATM System Operational and Technical Requirements

ED-137 – Interoperability Standards for VoIP ATM Components (in order to prove adherence with ED-137 standards, the tenderers shall submit together with the tender response the testing results from the EUROCONTROL VOTER testing tool)

ED-138 – Network Requirements and Performances for VoIP ATM Systems

ED-139 – Qualification tests for VoIP ATM Components and Systems

Recommendations of Eurocontrol

Regulation (EU) 2018/1139

Regulation (EU) 2017/373

RDST0020	The equipment shall also meet the following standards for electrical safety:

IEC 60950 – International Safety Standard for Information Technology Equipment EN 60215.

RDST0030	The VCS equipment shall be newly-produced and shall meet the requirements for ground based aeronautical stations laid down in standard documents listed in RDST0010.

RDST0040	The Contractor shall comply with the EMC/EMI directives.

### Regulatory Documents

RDRD0020	The offered concept, design and equipment shall be fully compliant with Directive 2014/30/EU of the European Parliament and of the Council of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast) (OJ L OJ L 96, 29. 3. 2014, p. 79), as last amended by the Regulation (EU) 2018/1139 of the European Parliament and of the Council of 4 July 2018 on common rules in the field of civil aviation and establishing a European Union Aviation Safety Agency, and amending Regulations (EC) No 2111/2005, (EC) No 1008/2008, (EU) No 996/2010, (EU) No 376/2014 and Directives 2014/30/EU and 2014/53/EU of the European Parliament and of the Council, and repealing Regulations (EC) No 552/2004 and (EC) No 216/2008 of the European Parliament and of the Council and Council Regulation (EEC) No 3922/91(OJ L 212, 22. 8. 2018, p. 1).

RDRD0030	The offered concept, design and equipment shall be fully compliant with the latest ED-137 Interopability Standards for VoIP ATM Components Part 1.

RDRD0040	The offered training for the equipment shall be fully compliant with the ATSEP.OR.215 System and equipment rating training requirement of the Commission implementing regulation (EU) 2017/373 of 1 March 2017 laying down common requirements for providers of air traffic management/air navigation services and other air traffic management network functions and their oversight, repealing Regulation (EC) No 482/2008, Implementing Regulations (EU) No 1034/2011, (EU) No 1035/2011 and (EU) 2016/1377 and amending Regulation (EU) No 677/2011 (OJ L 62, 8. 3. 2017, p. 1), as last amended by the Commission Implementing Regulation (EU) 2020/469 of 14 February 2020 amending Regulation (EU) No 923/2012, Regulation (EU) No 139/2014 and Regulation (EU) 2017/373 as regards requirements for air traffic management/air navigation services, design of airspace structures and data quality, runway safety and repealing Regulation (EC) No 73/2010 (OJ L 104, 3. 4. 2020, p. 1).

## Definitions

| Term/Phrase | Definition |
| --- | --- |
| Availability | A measure of the degree to which an item is in an operable state at any time. |
| Reliability | The probability that an item will perform its intended function for a specified interval under stated conditions. |
| Maintainability | A measure of the ability of an item to be retained in, or restored to, a specified condition when maintenance is performed using prescribed procedures and technician skill levels. |
| Consumable spare | Expendable item, such as fuses, lamps, air filters, etc., that can be easily replaced by use of standard tools and procedures. |
| Civil Aviation Authority | Republic of Slovenia, Civil Aviation Agency |

Note: Terms “Tenderer”, “Contractor”, “Manufacturer” and “Supplier” are synonims and shall mean entity, acting as bidder for public tender / entity, which implements public procurement.

## Abbreviations

| Abbreviation | Meaning, description |
| --- | --- |
| ACC | Area Control Centre |
| AC | Alternating Current |
| A/G | Air-Ground communication |
| AIS | Aeronautical Information Service |
| ANSP | Air Navigation Service Provider |
| ATCC | Air Traffic Control Centre |
| ATCO | Air Traffic Controller |
| ATM | Air Traffic Management |
| ATS | Air Traffic Service |
| ATSEP | Air Traffic Safety electronics personnel |
| ATSN | ATS Network |
| BITE | Built-in Test Equipment |
| BSS | Best Signal Selection |
| CD | Compact Disc |
| COTS | Commercial-Of-The-Shelf |
| CPU | Central Processing Unit |
| CSCI | Computer Software Configuration Item |
| DA | Direct Access |
| DT | Delivery Time. Defined as the time elapsed between the date of order of a part by the Contracting authority (in case of need of the order of additional spare parts) and the date of shipment of ordered part from the Contractor to the Contracting authority. |
| DC | Direct Current |
| DTMF | Dual Tone Multi Frequency |
| EATMN | European Air Traffic Management Network |
| EMP | Electromagnetic pulse |
| FAT | Factory Acceptance Test |
| FXS | Foreign eXchange Subscriber |
| G/G | Ground-Ground communication |
| GUI | Graphical User Interface |

| HMI | Human Machine Interface |
| --- | --- |
| HW | Hardware |
| IA | Instantaneous Access, Indirect Access |
| IP | Internet Protocol |
| ISDN | Integrated Services over Digital Network |
| IT | Information Technology |
| LAN | Local Area Network |
| LB | Local Battery |
| LCD | Liquid Crystal Display |
| LED | Light Emitting Diode |
| LRU | Line Replaceable Unit that is repairable and that shall: - in case of failure be identified by the Built-In-Test-Equipment (BITE) monitoring system, with the help of Technical Manual(s) and use of standard tool; - be easily accessible and replaceable (e.g. plug-in unit, screwed terminals or connectors); - have minimal adjustment requirements (e.g. voltage level setting, etc.) - be designed in such a way to ensure that the system returns to its full operational status within a meantime of 60 minutes (MTTR < 1 hour) when only one LRU has failed. |
| MFC | Multi Frequency Code |
| MRT | Mean Response Time in hours (i.e. the average time from notification of failure for a technician to be ready to commence repair action). |
| M/S | Main/Standby |
| MTBF | Mean Time Between Failures. A basic measure of reliability for repairable items. The average time during which all parts of the item perform within their specified limits, during a particular measurement period under stated conditions. |
| MTTR | Mean Time To Repair. A basic measure of maintainability. The sum of corrective maintenance times divided by the total number of failures within an item. The average time it takes to fully repair a failed system. Typically includes fault isolation, remove and replacement of failed item(s) and checkout. It excludes logistics downtime needed for spare part transport from stock to the site. |
| NTP | Network Time Protocol |
| OP/CO | Operator/Coach |
| OWP | Operator Working Position |
| PABX | Private Automatic Branch eXchange |
| PC | Personal Computer |
| PMP | Project Management Plan |
| PSTN | Public Switched Telephone Network |
| PTT | Push-To-Talk |
| QSIG | Q Signaling |
| RAM | Reliability, Maintainability and Availability |
| RX | Receive, Receiver |
| SAT | Site Acceptance Test |
| SIP | Session Initiation Protocol |
| SLA | Service Level Agreement |
| SNMP | Simple Network Management Protocol |
| SOC | Security Operations Center |
| SRU | Shop Replaceable Unit, defined as a unit which is replaced within a LRU and is repairable. |
| SW | Software |
| SWAL | Software assurance level |
| TAT | Turn-Around-Time. The time elapsed between the date of arrival of the faulty item at repair workshop and the date of shipment of the repaired (or replaced) item from the repair workshop to the Contracting authority. |
| TCP | Transmission Control Protocol |
| TDM | Time Division Multiplexing |
| TED | Touch Entry Device |
| TFT | Thin Film Transistor |
| TMCS | Technical Monitoring and Control System |
| TWR | Air traffic control tower |
| TX | Transmit, Transmitter |
| UHF | Ultra High Frequency |
| UI | User Interface |
| USB | Universal Serial Bus |
| URI | Uniform Resource Identifier |
| VCS | Voice Communication System |
| VHF | Very High Frequency |
| VoIP | Voice over IP |
| VOTER | VoIP in ATM Test Suite |
| WAN | Wide Area Network |

# System Architecture

## System Structure

The offered VCS shall provide a fully, automatic redundant architecture, based in two (2) datacenters, where the connected tower positions in Portorož and Maribor are using the infrastructure of the datacenter to minimize the necessary IT components at the local site. The redundancy requirements shall apply to the equipment in each datacenter and between the datacenters, as well.

All sites shall be interconnected via a redundant WAN, which is provided by the customer.

Drawing of the new Operational system

Drawing of the new Training system

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SYAR0010 | The system shall use a decentralized distributed architecture. |  |
| SYAR0020 | The system shall support the protocols/specifications disclosed in EUROCAE ED-137B/C (VoIP). |  |
| SYAR0030 | Connection between central equipment and positions shall be duplicated in order to prevent a total disconnection of positions in case of single cable interruption. If additional equipment is needed between central equipment and positions, that equipment shall be duplicated as well. |  |
| SYAR0040 | Each position shall remain operational even with single connection to the central equipment. |  |
| SYAR0050 | Connection between positions and central equipment shall be provided in a way that removal or failure of one or any number of positions shall not have any impact on the operability of the system and on the remaining positions. |  |
| SYAR0060 | Replaceable modules shall be of hot-pluggable design to enable inserting and/or pulling out the modules without the need to restart any other part of the system during normal operation. |  |
| SYAR0070 | Any functional elements within central equipment (e.g. power supply) shall not be a single point of failure. |  |
| SYAR0080 | The system to be offered shall be modular in design so as to be adaptable in the event of re- arrangements of positions, frequency channels and functions. It shall also be flexible in its channel-to-position allocation part. |  |
| SYAR0090 | The Contractor is solely responsible for the System Design. If any changes to the design are necessary to meet the Specifications, the Contractor shall carry out such changes at no cost to the Contracting authority. |  |
| SYAR0100 | The Contractor shall be responsible for the system engineering efforts associated with the design, production, installation, testing and audit of the systems and equipment being provided. |  |
| SYAR0110 | The Tenderer shall deliver a detailed rack layout and equipment placement scheme for every location, from which the placement of all equipment shall be clearly visible inside the object and each telecommunication rack. |  |
| SYAR0120 | The Tenderer shall design a VCS according to the specified system described in this document and in its attachment diagrams. |  |
| SYAR0130 | The VCS shall comply with EUROCAE ED-137 standard and shall be compatible with the Rohde & Schwarz 4200 series radios, operating at Slovenia Control local sites and remote communications sites. |  |
| SYAR0140 | The VCS should support the following remote-control functions on the radios: - Manual change of the frequency in the Aeronautical band for each radio; - Selection of a frequency from a predefined list; - Radio preset page selection; - Monitoring radio status OK/WARNING/ERROR; - Enable/disable the squelch; - Adjust the transmit power level of each radio; - Adjust the reception sensitivity of each radio. |  |

## System Restart

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SYRE0010 | All user specified data, which is representing the actual status of the system, shall be stored in non-volatile and protected memory space. |  |
| SYRE0020 | After an automatic or manual reset of the system the last configuration, which was active before the restart, shall be activated. |  |
| SYRE0030 | Global restart of the system shall be completed within less than 7 minutes. |  |

## System Software

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SYSW0010 | The software shall be designed to provide reliability, error detection, fault tolerance and recovery. |  |
| SYSW0020 | The software shall be in accordance with Commission Regulation EC 482/2008. |  |
| SYSW0030 | The system software shall be developed, supplied and maintained in accordance with the objectives as defined in ED153 for SWAL3. |  |
| SYSW0040 | Supplier demonstration of ED153 objectives for SWAL3 fulfilment is a necessary condition for system acceptance. |  |
| SYSW0050 | The software shall be modular, with respect to structure, coding, testing and interaction between the different parts of the system. |  |
| SYSW0060 | Unique application software shall be based on proven technology. |  |
| SYSW0070 | The operating system to be utilized shall be totally proven in a similar environment. |  |
| SYSW0080 | The system shall be such, that new versions of all software types (operating system, application, configuration, maintenance) can be loaded and tested without detriment to the operational service. |  |
| SYSW0090 | The system configuration data shall allow the making of offline configurations and the backup of the active configuration. |  |
| SYSW0100 | It shall be possible to restore the configuration from an offline or stored version. |  |
| SYSW0110 | System maintenance software shall be available. This software shall run in background and shall have no detrimental effect on any system processing. |  |
| SYSW0120 | The system maintenance software shall provide self-diagnostic capabilities, with the ability to detect failures. |  |
| SYSW0130 | The system maintenance software shall include facilities for activity and event logging. There shall be capability for activity and event logging for at least 30 days. |  |
| SYSW0140 | It shall be possible to extract this information from the system in a suitable industry standard format, for off-line statistical analysis, without in any way affecting the operational service. |  |
| SYSW0150 | Software licenses for all software delivered (system, TMCS, HMI prototyping) shall be included in the offer. |  |

## System capacity

### Operator Working Positions

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSOP0010 | The number of Operator Working Positions that shall be delivered together with the Operational system is shown in the Table 1. |  |

| Location | Nr. Of Positions | Extension Capability |
| --- | --- | --- |
| ACC Room | 20 | 32 |
| Tech Room | 3 | 5 |
| AIS | 2 | 3 |
| TWR Brnik | 4 | 5 |
| TWR Portorož | 3 | 4 |
| TWR Maribor | 4 | 5 |
| Datacenter 2 | 2 | 4 |
| TOTAL | 38 | 58 |

Table 1: Operator Working Positions for the Operational system

Note: Extension Capability means the delivered system needs to be able to support this number of positions without the need for major system upgrades (e.g. servers do not need to be exchanged). Cabling, Position hardware and licences are not required to be foreseen in advance.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSOP0020 | The number of Operator Working Positions that shall be delivered together with the Training and Test system is shown in the Table 2. |  |

| Location | Nr. Of Positions | Extension Capability |
| --- | --- | --- |
| ACC Simulator | 11 | 13 |
| TWR Simulator | 2 | 4 |
| AdaaS project | 8 | 10 |
| Test System | 2 | 4 |
| TOTAL | 23 | 31 |

Table 2: Operator Working Positions for the Training and Test system

### Audio devices

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSAD0010 | Each Operator Working Position shall be equipped with 1 loudspeaker and the possibility to connect up to 4 audio devices (e.g. microphone, handset, headset). |  |
| SSAD0020 | The number of audio devices that shall be delivered together with the VCS system (Operational + Training and Test system) is shown in the Table 3. |  |

| Devices | Nr. of Devices |
| --- | --- |
| Microphone | 100 |
| Handset | 110 |

Table 3: Audio devices for the VCS system

Note: The table above already includes spare devices. Audio devices defined above do not need to be foreseen in the spares calculation of the system.

### Interfaces

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSIN0010 | The number of interfaces that shall be delivered together with the Operational system for ATCC and TWR Brnik is shown in the Table 4. |  |

| Type of Interface | Nr. of lines | Extension Capability |
| --- | --- | --- |
| Native IP (ED-137) radio channels | 64 | 78 |
| Analog radio lines (4 wire inband) | 18 | 20 |
| IP Telephone channels (SIP, ED-137) | 40 | 50 |
| QSIG lines | 4 | 8 |
| MFC lines | 8 | 12 |
| FXS lines | 4 | 8 |
| PSTN/PABX lines | 4 | 8 |
| LB lines | 0 | 0 |

Table 4: Interfaces for the Operational system – ATCC and TWR Brnik

Note: Extension Capability means the delivered system needs to be able to support this number of interface lines without the need for major system upgrades (e.g. servers do not need to be exchanged, shelve space and power supply for additional cards foreseen). Cabling, Line Interface Cards and licences are not required to be foreseen in advance.

Note: radio channel means number of individual radio devices to be connected to the system (e.g. sum of RX A, TX A, RX B and TX B radio devices).

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSIN0020 | The number of interfaces that shall be delivered together with the Operational system for TWR Portorož is shown in the Table 5. |  |

| Type of Interface | Nr. of lines | Extension Capability |
| --- | --- | --- |
| Native IP (ED-137) radio channels | 8 | 10 |
| Analog radio lines (4 wire inband) | 0 | 0 |
| IP Telephone channels (SIP, ED-137) | 3 | 4 |
| QSIG lines | 0 | 0 |
| MFC lines | 2 | 4 |
| FXS lines | 2 | 4 |
| PSTN/PABX lines | 2 | 4 |
| LB lines | 0 | 0 |

Table 5: Interfaces for the Operational system – TWR Portorož

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSIN0030 | The number of interfaces that shall be delivered together with the Operational system for TWR Maribor is shown in the Table 6. |  |

| Type of Interface | Nr. of lines | Extension Capability |
| --- | --- | --- |
| Native IP (ED-137) radio channels | 8 | 10 |
| Analog radio lines (4 wire inband) | 0 | 0 |
| IP Telephone channels (SIP, ED-137) | 3 | 4 |
| QSIG lines | 0 | 0 |
| MFC lines | 0 | 0 |
| FXS lines | 2 | 4 |
| PSTN/PABX lines | 2 | 4 |
| LB lines | 0 | 0 |

Table 6: Interfaces for the Operational system – TWR Maribor

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSIN0040 | The number of interfaces that shall be delivered together with the Training and Test system is shown in the Table 7. |  |

| Type of Interface | Nr. of lines | Extension Capability |
| --- | --- | --- |
| Native IP (ED-137) radio channels | 20 | 30 |
| Analog radio lines (4 wire inband) | 8 | 12 |
| IP Telephone channels (SIP, ED-137) | 3 | 4 |
| QSIG lines | 2 | 4 |
| MFC lines | 2 | 4 |
| FXS lines | 2 | 4 |
| PSTN/PABX lines | 2 | 4 |
| LB lines | 0 | 0 |

Table 7: Interfaces for the Training and Test system

### TMCS

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSTM0010 | The number of TMCS clients that shall be delivered together with the Operational system is shown in the Table 8. |  |

| Location | Nr. of clients |
| --- | --- |
| Tech Room (Datacenter 1) | 2 |
| Datacenter 2 | 1 |
| ACC | 1 |
| TWR Portorož | 1 |
| TWR Maribor | 1 |
| TOTAL | 6 |

Table 8: TMCS clients for the Operational system

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SSTM0020 | The number of TMCS clients that shall be delivered together with the Training and Test system is shown in the Table 9. |  |

| Location | Nr. of clients |
| --- | --- |
| Tech Room (Datacenter 1) | 1 |

Table 9: TMCS clients for the Training and Test system

# System Deployment

The Voice Communication System is functionally divided into the following groups:

- Operator working position equipment;

- Interface equipment;

- Data exchange equipment;

- Technical Monitoring and Control equipment.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SYDE0010 | Technical Monitoring and Control System – The VCS shall be provided with a physically distinct configuration, monitoring and maintenance system. |  |
| SYDE0020 | VCS Operator Working Positions – The VCS shall include all nominated local and remote VCS OWPs as listed in the section on System capacity. |  |
| SYDE0030 | Connectivity to neighboring VCS for the future framework of inter-VCS interoperability – Voice system resources/features shall include: - RX and TX radio channels (according to ED-137); - Support for inter-VCS position monitor function (according to ED-137). |  |
| SYDE0040 | Data communication protocols between VCS and other subsystems – Unless explicitly specified otherwise, all data connectivity external to VCS shall be based on TCP/IP protocol. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SYDE0060 | Radio (RX, TX and transceivers) connectivity for Operational VCS – The Operational VCS shall offer connectivity to all nominated local and remote Ground Radio Stations. A radio voice aggregation solution shall be provided to reduce bandwidth required to connect to remote VoIP radios. |  |
| SYDE0070 | Radio connectivity for testbed (test system) VCS – The testbed VCS shall offer simulated and real connections to the Ground Radios as well as connectivity to future TB Ground Radio Stations. |  |
| SYDE0080 | Telephone connectivity – The VCS shall offer telephone connectivity to the external world by way of leased lines and shared networks (including PSTN). It shall however be possible to fully operate the VCS without connectivity to public (e.g. PSTN) networks. |  |
| SYDE0090 | The VCS shall provide integrated IP PABX functionalities to the VCS telephone users. The VCS IP PABX shall provide a Session Border Controller function (SBC) for any connection to external non-private WAN networks. |  |
| SYDE0100 | The VCS IP PABX shall be able to provide the following functionalities: - Call Admission Control – limits the number of calls via particular SIP trunk or to a particular device to a given number; in case the maximum number of calls is reached, it denies the new call or reroutes the call via another SIP trunk; - Intrusion Detection; - Multiple Configration sets with fast switching between the configurations (approx. 5 seconds); - Call forking; - Call rerouting; - Alternate routing; - Network separation. |  |
| SYDE0110 | The VCS IP PABX shall provide network translation (NAT) at IP and SIP level in order to keep the internal network details hidden. The translation shall be available for both IPv4 and IPv6 versions. Also, the VCS IP PABX shall provide protection against theft of service. |  |
| SYDE0120 | The VCS IP PABX shall support transcoding/translating between ED-137 defined codecs (G.728, G.729, G.711A and G.711U). |  |
| SYDE0130 | In case the IP VCS core telephone communication fails, the OWPs should be able to establish SIP/RTP connections directly, with other G/G peers, according to ED-137. |  |
| SYDE0140 | The Session Border Controller (SBC) facilty of the VCS IP PABX should support SIP Authentication via SIP Register. |  |
| SYDE0150 | The Session Border Controller (SBC) facility of the VCS IP PABX should be able to limit the traffic from defined IP addresses using internal firewall. |  |
| SYDE0160 | The Session Border Controller (SBC) facility of the VCS IP PABX should support the marking of the RTP traffic. It is foreseen to use EF flag to expedite forwarding of the RTP flows. |  |
| SYDE0170 | The Session Border Controller (SBC) facility of the VCS IP PABX should support load balancing of multiple SIP Tunks to distribute the traffic across them equally. |  |
| SYDE0180 | The Session Border Controller (SBC) facility of the VCS IP PABX should be use SIP trunk digest authentication via SIP Register. |  |

## Structure and redundancy of the system

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| STRE0010 | Decentralized and distributed structure – The VCS shall have a distributed architecture with intelligent end-points that holds a complete and valid copy of the overall VCS communication dial-plan and its own configuration data during operation. |  |
| STRE0020 | Modularity and flexibility – The VCS shall be modular, flexible and easy to configure. |  |
| STRE0030 | Logical connection flexibility – The VCS design shall support the assignment of a logical connection between a VCS OWP and a radio channel to any physical radio interface without any restriction. The VCS design shall also support the assignment of a logical connection between a VCS OWP and a telephone channel to any physical telephone interface without any restriction. Radio and telephone channels are constituents of frequency and trunk objects respectively. |  |
| STRE0040 | Logical connection redundancy – Logical connections between a VCS OWP and a radio channel, shall be routed via at least 2 independent physical paths for redundancy purposes. |  |
| STRE0050 | Expandability – The VCS shall be designed to support future expansion in terms of: - External interfaces: to connect to neighboring VCSs, Ground Radio Stations and telephones; - Operator Working Positions. |  |
| STRE0060 | Redundancy of the Operational VCS – The Operational VCS shall have sufficient redundancy to prevent the outage of a critical function or degradation of the capacity due to single system component failure. |  |
| STRE0070 | Operational VCS sub-systems interconnection – As a minimum the connections between different Operational VCS equipment items shall be duplicated. |  |
| STRE0080 | Description of redundancy – The VCS core equipment (servers) shall be distributed in two redundant geographical locations (datacenters), whereas each location contains redundant equipment. The switchover between datacenters in case of data center faiure shall be executed automatically, with no intervention from the operators or system administrators. The OWPs and the other system end-points (e.g. gateways) shall be able to access resources from both datacenters. |  |
| STRE0082 | The core equipment in datacenter 2 shall have the same capacity as in datacenter 1 to support all OWPs in ATCC and airports. |  |
| STRE0084 | The configuration items in datacenter 1 - redunant core shall be replicated in real time in the datacenter 2 - redundant core equipment. |  |
| STRE0086 | For greater availability of air-ground calls, Radio Services equipment in both datacenter 1 and datacenter 2 shall initiate permanent radio sessions to radio resources (IP radios or Radio Gateways). In case the Radio Service equipment in one datacenter fails, the Radio Service equipment from the datacenter 2 shall immediately reinitiate the radio call to the OWPs. |  |
| STRE0088 | For greater availability of the ground-ground calls to external destinations, these calls shall be replicated inside the Telephony Service core in one datacenter. In case the Telephony Sevice in the respective datacenter fails, the call shall be reinitiated manually by using the Telephony Service core in the second datacenter. |  |

## Structure and Redundancy of external connectivity

The requirements below specify how VCS interfaces have to be connected to external components using Voice over internet protocol (VoIP).

| ID | Requirements |  | Compliance YES/NO – references to evidence |
| --- | --- | --- | --- |
| STRE0090 | Redundancy of connectivity to a neighboring VCS or fallback solution in-country in the framework of inter-VCS interoperability shall be supported. |  |  |
| STRE0100 | Redundancy of physical network connectivity to each ground radio – Connection to ground radio shall support redundant physical connections via the operational network (for the locations where the radios support 2 physical IP connections). |  |  |

## Robustness and Behaviour

The system architecture shall be such that it fulfils all performance and operational requirements as well as the Availability, Reliability, Maintainability requirements as stated throughout this specification.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| ROBE0010 | VCS operational hours – The VCS shall be designed for continuous operation 24/7 (24 hours a day, 365 days a year). |  |
| ROBE0020 | The VCS shall be designed that in case of maintenance, server replacement, complete failure or loss of one data center the system will provide service continuity to its users (Continuity of Service) due to system redundancy. |  |
| ROBE0030 | Non-blocking system – The VCS shall be a non-blocking system for all types of messages (refer to Note 1) by providing enough resources (refer to Note 2) while operating at any load condition, including the maximum load scenario, and while operating in any configuration, including the maximum capacity configuration. |  |

Note 1: By use of the term “messages” in this context it is understood, but not limited to: the voice communications between all system components, to/from external interfaces, messages to establish, maintain and clear the voice communications, including status, control and error messages.

Note 2: By use of the term “resources” in this context is understood, but not limited to: processing power, voice paths, time slots, bandwidth and memory.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| ROBE0040 | Maximum resource usage – Resource usage, while working in “normal operation”, shall not exceed 70% of the total resources while operating at any load condition, including the maximum load scenario, and while operating in any configuration, including the maximum capacity configuration. |  |

Note: Resources include CPU, disks, memory, disk storage, bandwidth, etc. The term ‘usage’ in this requirement is understood as the average of the instantaneous resource usage in a 5 s interval.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| ROBE0050 | Relevant parameters list – The VCS design shall be such that timing characteristics of restart and switch-over actions, which may be triggered by redundancy mechanisms or by manual commands, can be predicted. Values of these timing characteristics shall be listed. |  |
| ROBE0060 | Independence of system components – Faulty behavior of one system component shall not have any impact on the proper operation of another system component. Faulty behavior of auxiliary VCS system components (radio stations…) shall not be propagated by VCS to internal or auxiliary VCS components, affecting their proper operation. |  |
| ROBE0070 | Redundant inter-connection behavior – An unrecoverable fault with one of the redundant paths in the inter-connection between system components shall lead to an automatic transfer of data to another available path in the inter-connection and a notification being sent to the TMCS. |  |
| ROBE0080 | TMCS independence – Any failure in the TMCS shall not result in unavailability of any other part of the VCS and shall not lead to the loss of configuration or the loss of VCS services. |  |
| ROBE0090 | Single entity behavior – The VCS shall behave as a single entity regardless of the common or split installation of its redundant system components. |  |
| ROBE0100 | Autonomous operation of system components – Each individual system component shall act as an autonomous unit being equipped with its own processing capabilities to the maximum extent possible. |  |
| ROBE0110 | Ongoing communication shall not be dropped during main/standby switchover of the redundant VCS devices. Supplementary, the switchover between the redundant Ethernet interfaces of one device shall not cause ongoing calls to be dropped. No audible interruption of ongoing audio calls shall result. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| ROBE0120 | Continuity of operations – Loss of an individual physical connection to any system component shall not lead to any loss of communication nor configuration. |  |
| ROBE0130 | Continuity of operations with neighboring VCS (if implemented) – Loss of a connection to a neighboring VCS shall not impact the correct operation of the local VCS. Erroneous behavior or data overload by a neighboring VCS shall not impact the correct operation of the local VCS. |  |
| ROBE0140 | Availability of the external lines to redundant system components – The VCS shall make the access to/from a telephone line available to all of the involved redundant system components. |  |
| ROBE0150 | Availability of the radio stations to redundant system components – The VCS shall make access to/from the radio station available to all of the involved redundant system components. |  |
| ROBE0160 | Continuity of radio operations – Partial loss of a redundant connection to a remote radio shall not lead to any interruption of an active transmission or reception. |  |
| ROBE0170 | Sharing of radio resources – The neighboring VCS shall be able to access the available radio resources by utilizing the ED-137 radio standard. |  |
| ROBE0180 | Sharing of radio resources – The VCS shall be able to access the radio resources of a neighboring VCS. |  |
| ROBE0190 | Built-in fault detection for external connections – The VCS shall be able to monitor and report the status of all telephone and radio interconnections at the TMCS. |  |
| ROBE0200 | Built-in fault detection for internal system components – The VCS shall be able to monitor and report the status of major internal system components (interfaces, OWPs, etc.) at the TMCS. |  |

# Voice Communication System

## General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCGE0010 | The system shall consist of: - Operator Working Position (OWP) subsystem: The elements (devices such as microphones, speakers, and a touch screen) needed in the control room to enable the ATCO to interact with communication partners (e.g. aircraft, adjacent communication partners); - Monitoring and control subsystem: The elements needed to interact with the system for configuration, monitoring and control for technical supervision; - Communication backend subsystem: The elements needed to provide the interconnectivity between VCS elements and the communication resources (external and internal) that are to be used by the VCS. |  |
| VCGE0020 | The OWP subsystem shall be easy and comfortable to use and consist of a touch screen, loudspeaker and socket connectors for microphones, handsets and headsets. Solutions where the touch screen and the OWP processing unit are separate equipment are also accepted. |  |
| VCGE0030 | The monitoring and control subsystem shall be used for maintenance and configuration purposes. The following advanced control and monitoring functions shall at least be available: - Fast reconfiguration based on OWP roles; - Monitoring and configuration of working positions; - Configuration management servers; - Immediate alarm indication; - Event logging; - Layout for centralized preventive maintenance. |  |
| VCGE0040 | The access to monitoring and control subsystem shall be made available over web-based user interfaces. Configuration, Management and Monitoring shall not require any dedicated clients or any dedicated software applications. All tools shall be accessible via standard web-browsers. |  |
| VCGE0050 | The communication and management backend subsystem shall be embedded in a datacentre environment and consist of high available individual COTS hardware of configuration and call-related data. |  |
| VCGE0060 | The VCS system should support central user management with multiple roles by integration with AAA server (e.g. FreeRadius), for used authentication and authorization management. |  |
| VCGE0070 | The VCS system components should be able to use a so-called failsafe local startup configuration from their local memory in case of configuration server unavailability. |  |
| VCGE0080 | The VCS should have the possibility to run the central software application on a virtual environment based on virtual machines. |  |

## Legacy Interfaces

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCLI0010 | The system shall support: - ED-137B/C (VoIP) for ATM for phone and radio communications; - Radio Channels (VHF, UHF); - Analogue ATS MFC-R2; - Digital ATS-QSIG. |  |
| VCLI0020 | The legacy interfaces shall be connected to the IP network using redundant network connections, so that outage of network interface cannot cause loss of a complete interface shelf. |  |

## Communication Types

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCCT0010 | The system shall support bilateral radio communication in VHF and UHF range between ATC - aircraft crew and bilateral radio communication (ground to ground) between ATC - stationary and mobile objects. |  |
| VCCT0020 | The system shall support recording of radio exchange between contiguous ATCO points and radio channels (analogue and VoIP). |  |
| VCCT0030 | The system shall support internal intercom phone communication of system users. |  |
| VCCT0040 | The system shall support phone communication of system with connected subscribers (e.g. FXS/SIP). |  |
| VCCT0050 | The system shall support external phone communication with a PABX. |  |
| VCCT0060 | The system shall support direct access phone communication. |  |
| VCCT0070 | The system shall support telephone communication via PSTN. |  |

## Audio Quality

### Noise

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCAQ0020 | The weighted idle channel noise shall be < -65 dBm0 measured with a psophometric (C-weighted) measuring device. |  |

### Distortion

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCAQ0030 | Total Distortion, including quantizing distortion shall comply with ITU-T G.712. |  |

## Telephone and Intercom Services, Functions and Features

This section describes the functional and technical requirements for the telephone segment of the VCS.

Throughout this section the term “key” refers to an appearance on a touch screen. The term “call” refers to a G/G calls.

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0010 | The VCS shall permit simultaneously operation of all operational positions to either place calls, receive calls, or both. |  |
| VCTF0012 | The operator shall be able to make and receive phone calls by the following means: - A handset; - A headset; - Simultaneous (for Trainer-Trainee function) use of: - 2 handsets, or - 2 headsets, or - one headset and one handset. |  |
| VCTF0020 | The system shall support the clear indication of the full phone number of an external calling station if available. |  |
| VCTF0030 | Incomming calls shall be presented by the VCS to the operator by an audible call-in chime and a visual indication. |  |
| VCTF0040 | The system shall support to mute incoming call chime when another call is already active. |  |
| VCTF0050 | It shall be possible to switch a phone call to the loudspeaker. |  |
| VCTF0060 | The system shall provide visual indication of the busy line status. |  |
| VCTF0070 | Trunk Routing – The system shall support trunk line hunting i.e. when an operator selects a specific trunk group for an outgoing call, the system will automatically look for a free line inside the group and seize that line. The system shall choose the first trunk in the configured list for call routing to a certain destination. Within a trunk, a trunk line shall be chosen for call routing in round robin manner. In case no free line can be found on this trunk, an alternative trunk shall be chosen. It shall be possible to form trunks including different interface types. |  |

### Direct access (DA)

The means by which, when accessing a single key, a connection is established to a predeterminated destination.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0080 | It shall be possible to assign a destination address to a DA key that shall enable the VCS to process and route calls accordingly. It shall be possible to assign an address that will route calls to a destination on the same VCS or to any external correspondent, using any type of supported telephone interface (ATSN, point to point lines, PSTN or other networks). |  |
| VCTF0090 | Direct Access Keys (Single destination DA according to ED-137) – Each OWP shall provide the capability of displaying and using at least 120 DA keys. |  |
| VCTF0092 | Each DA key shall allow for at least 20 alphanumerical characters arranged in 2 lines. |  |

#### Outgoing calls

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0100 | Upon operation of a DA key: - There shall be a unique visual indication that the particular DA key was accessed; - The identity of the called party shall be displayed in a display field. |  |
| VCTF0110 | When a connection to the called party is established the visual indication on the DA key shall change to notify user about successful connection. The active visual indication shall be present on the particular direct access key until the call has been terminated or transferred. |  |
| VCTF0120 | The identity of the B-party shall be displayed in a display field while the call is active. If the current call occupies a telephone line which is also available on DA mode at other positions, then at these other positions this key shall indicate that the line is occupied. |  |

#### Incoming calls

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0130 | The processing of incoming calls shall be dependent on received information regarding the identity of the calling party and of the call priority, if that information is available. |  |
| VCTF0140 | An incoming call from the A-party shall appear on the same DA key that is used for an outgoing call to that destination. |  |
| VCTF0150 | On arrival of an incoming DA call: - There shall be a unique visual indication and audible warning, that there is an incoming call on a particular direct access key; - The identity of the calling party shall be displayed in a display field. |  |
| VCTF0160 | Upon accessing of that DA key: - The operator shall be connected to the calling party; - The visual status on the DA key shall change to show the call is active and any audible warning shall cease; - The identity of the called party shall be displayed in a display field while the call is active; - These indications shall remain active until the call has been terminated or transferred. If the current call occupies a telephone line which is also available on DA mode at other positions, then at these other positions this key shall indicate that the line is occupied. |  |

### Indirect access (IA)

#### Outgoing calls

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0170 | Indirect Access Keys (Instantaneous Access according to ED-137) – Indirect Access keys. Each OWP shall provide the capability to enable the operator to initiate a call by dialing its number manually on a dial pad. |  |
| VCTF0180 | To establish a dialed connection, it shall be necessary to dial the complete number. |  |
| VCTF0190 | If the call is external to the system and the ATS network, it will be necessary to select a particular network. This shall be achieved by either operating a particular network key, or dialing an access code. |  |
| VCTF0200 | Upon accesing the dial pad and dialing the complete number: - The call shall appear in an active call area and there shall be a visual indication to show the call is active; - There shall be a visual indication to show there is an active call at the position. |  |
| VCTF0210 | When a connection to the called party is established the visual indication on the active call area shall change to notify user about successful connection. The active visual indication shall be present on the active call area until the call has been terminated or transferred. The identity of the B-party shall be displayed in a display field while the call is active. |  |

#### Incoming calls

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0230 | Incoming calls which are not presented on a DA key shall be presented on an incoming call queue. |  |
| VCTF0240 | Calls shall be presented on call queuing keys, providing the user with information regarding the calls, to enable selective answering. |  |
| VCTF0250 | The operator shall be able to accept pending calls in any order. |  |
| VCTF0260 | If there is assignment between the name and the number of calling party, the name shall be displayed in the call queue (if defined in the system internal phonebook), otherwise the caller number shall be displayed. |  |
| VCTF0270 | If no information about the identity of the caller is available, at least global identity (e.g. name of ANSP, line of PSTN) shall be displayed to indicate the generic source of the call. |  |
| VCTF0280 | All calls in the queue shall remain in pending (ringing) condition until answered or terminated. |  |
| VCTF0290 | Active calls and calls in hold condition shall remain in the queue until the call is finished. |  |
| VCTF0300 | Size of the call queue shall be at least 5 incoming calls. |  |

### Call timeout

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0302 | If after initiation of a call set up or function request the user does not enter a complete required input within a certain period, the system shall terminate the call set up procedure or function request. |  |
| VCTF0304 | The value of this period shall be configurable. |  |

### Redial

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0310 | Last Number Redial – This function shall allow the user to redial the last number dialled on the dial pad by pressing a single key. A list of the last incoming and outgoing calls shall be available, even for unsuccessful calls. |  |

### Numbering scheme

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0326 | The system shall support a closed numbering scheme. The system numbering scheme shall support sufficient digits in order to comply with ITU-T Recommendation. |  |
| VCTF0327 | The numbering scheme shall support the following: - Conformance with the ATSN numbering scheme; - Internal numbering of terminals and interfaces; - Prefixes to access other networks including the PSTN; - Prefixes to access system functions and facilities. |  |
| VCTF0328 | The system shall include a look up table to allow correlation of telephone numbers with full operational names and the mnemonics to be displayed on the DA and queue keys. This table shall allow for at least 2000 entries. |  |

### Hotline

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0330 | For the establishment of hotline mode, it shall be needed to use only one key. |  |
| VCTF0340 | An incoming hotline call shall be immediately routed to a dedicated loudspeaker at the called position. |  |
| VCTF0350 | An outgoing hotline call shall be directly connected to the correspondent line interface (transmit audio only). |  |
| VCTF0360 | An internal hotline call shall establish one way communication from the caller to the called positions. |  |
| VCTF0370 | The hotline keys shall be visually differentiated from normal keys. |  |
| VCTF0380 | The hotline keys shall work in a PTT mode (the call shall only be active while the key is pressed, releasing the hotline key shall automatically release the call). |  |
| VCTF0390 | On an internal hotline call, the identity of the caller party shall be indicated at the called position. |  |

### Priority

This function provides users a guaranteed connection between internal working positions, or externally, over the Air Traffic Services Network, on circuits that support priority calling (MFC and ATS-QSIG).

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0410 | The system shall support a Priority key for emergency calls in case the other side is busy. A priority key shall be possible to prioritize any call made by DA key or otherwise. |  |
| VCTF0412 | Each position (or position configuration) shall be assigned a priority level for routine calls. |  |
| VCTF0414 | The VCS shall include the priority level of the terminal in all call set up requests. |  |
| VCTF0420 | There shall be a unique visual indication for an outgoing call with the highest priority in order to distinguish from routine calls. |  |
| VCTF0430 | On an incoming call, at the called party, special audible and visual indications shall be used for identifying that a call with higher priority is waiting to be answered. |  |

### Transfer (Call forwarding)

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0440 | This function shall enable any active call at a working position to be manually redirected to any other party, via any type of interface. |  |
| VCTF0450 | This function shall be available for both outgoing and incoming calls. |  |
| VCTF0460 | After transfer, the call shall be presented at the new position in the same way as if it was made originally for that position. |  |

### Hold

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0470 | The hold function shall allow a user to disconnect temporarily from an established call without releasing it. |  |
| VCTF0480 | During hold condition, the operator shall be able to perform other radio or telephone functions. |  |
| VCTF0490 | No audio shall be transmitted to the correspondent that was put on hold condition. |  |
| VCTF0500 | It shall be possible to put any active call on hold (DA and IA, incoming and outgoing), with the exception of hotline calls. |  |
| VCTF0510 | If after the call is put on hold, the operator engages on another telephone call, it shall be possible to toggle between both telephone calls. |  |
| VCTF0520 | At the position, there shall be a visual indication of the hold condition. |  |
| VCTF0530 | The other party shall get audible information that the call is on hold. |  |

### Conference

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0540 | Using a simple and intuitive conference page, the conference originator shall be able to add or remove conference participants from the conference. |  |
| VCTF0550 | This function shall enable a user to interconnect a number of operator working positions and/or lines of varying types, allowing full speech facilities to all connected parties. |  |
| VCTF0560 | It shall be possible to initiate a conference independent of whether the first call is incoming or outgoing. |  |
| VCTF0570 | It shall be possible for the conference originator to add individual conference participants one by one. |  |
| VCTF0580 | It shall be possible to establish a conference with up to 5 participants. |  |
| VCTF0590 | Any conference participant shall be able to leave the conference at any time by terminating the call. |  |
| VCTF0600 | It shall be possible to add preset conferences using the configurator. Preset conferences consist of pre-defined members which will be automatically called and added to the conference upon dialling the configured conference URI. When a preset conference is ongoing, subsequent parties that dial the preset conference URI are added to the conference automatically. By means of the conference function it shall be possible that several parties can share a common communication channel that enables them to simultaneously talk to each other. The VCS shall support up to 20 parties within a single conference. |  |

### Call pickup

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0610 | Each operator shall be able to pick up a selective call that is pending at other positions. Call Pickup shall not be applied to Instantaneous Access call or Position Monitoring calls. |  |
| VCTF0620 | Only unanswered calls at that time shall be picked up. |  |

### Call divert

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0630 | A divert key shall be available, and shall enable an automatic redirection of all new incoming selective telephone calls to another operator working position of the VCS. |  |
| VCTF0640 | The divert function shall work for all type of calls, except hotline calls. |  |
| VCTF0650 | The divert function shall be activated by pressing the divert key and then selecting the destination operator working position.The destination position shall be selectable by pressing the DA key or dialing the IA call number. |  |
| VCTF0660 | When a position has activated divert, outgoing calls shall still be possible. |  |
| VCTF0670 | The VCS shall provide a visual indication on the divert key at the forwarding position when this function has been activated. Also the identity of the destination where calls are to be diverted shall be displayed permanently in a display field while the diversion is active. |  |
| VCTF0680 | The VCS shall support chaining of diversion. |  |
| VCTF0690 | Diversion chains that result in loops shall be prohibited by the system. |  |
| VCTF0700 | It shall also be possible for different positions to simultaneously divert to the same destination position. |  |
| VCTF0710 | It shall be possible to configure this function to work also for no response situations. |  |

### Parallel signaling

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0720 | This function when configured shall signal all incoming calls intended for a role belonging to a parallel signaling group at all positions. |  |
| VCTF0730 | The first of the predefined positions that answers the call shall be connected to the caller, all call waiting indicators shall be cleared at the other positions. |  |
| VCTF0740 | It shall be possible to assign a role to more than one parallel signaling group simultaneously. |  |

### Position monitoring

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0750 | The system shall support monitoring according to ED-137 to enable monitoring of all audio at the monitored position. By means of a Position Monitoring function an operator shall be able to listen to the selective A/G or G/G audio as well as combined audio of G/G and A/G communication of up to 3 different operator working positions. |  |
| VCTF0770 | The identity of the operator working position to be monitored shall be displayed. |  |
| VCTF0780 | An indication on the position which is monitored shall be displayed. |  |

### Telephone book

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0790 | The telephone book shall provide the operator with the possibility to choose telephone targets from a pre-configured list. |  |
| VCTF0800 | While searching through the telephone book, it shall provide search-as-you-type entry lookup functionality for faster access to known numbers. |  |
| VCTF0810 | It shall be possible to perform a direct call from the telephone book. |  |

### End key

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0840 | An End key shall be available. The End key shall be the means by which active calls can be terminated. |  |
| VCTF0850 | The End key shall also terminate outgoing calls that have been initiated but not yet answered. |  |
| VCTF0860 | The operator shall have a possibility to terminate any active call, independently of the originator of the call. |  |

### Call reporting

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTF0880 | A list of answered and unanswered (outgoing and incoming) calls shall be available at each position |  |
| VCTF0890 | The list shall include A and B party identification, start time and duration of the call if available. |  |

## Radio Services, Functions and Features

This section describes the functional and technical requirements for the radio segment of the VCS.

Throughout this section the term “key” refers to an appearance on a touch screen.

The VCS shall support VoIP radio connectivity according to ED-137B/C (for backward compatibility reasons).

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0010 | The VCS shall permit simultaneously operation of all operational positions to transmit and receive radio calls. |  |
| VCRF0020 | At least 25 radio channels shall be available at each position. At least 5 radio sites can be configured for each frequency. |  |
| VCRF0030 | Radio Sources – The system operator shall be able to select between the following radio sources: - operational receivers; - operational transmitters. In future, it shall be possible to add additional sources when available. The number of frequencies available for simultaneous selection at the working position shall be up to 16. |  |
| VCRF0040 | It shall be possible to assign a radio channel to all operator working positions at the same time. |  |
| VCRF0042 | The operator shall be able to communicate via frequencies or channels by using: - A microphone and a loudspeaker; - Two microphones (one microphone for the coach and one for the trainee) and a loudspeaker; - A handset with integrated microphone and integrated loudspeaker and a PTT switch; - A headset with attached PTT switch. |  |
| VCRF0043 | When using a headset, it should be possible to select to simultaneously listen to the frequency using the integrated loudspeaker. |  |
| VCRF0050 | In the profile of the role (defined in the TMCS) it shall be possible to restrict the available frequencies which can be used for this role. |  |
| VCRF0060 | Frequency coverage – The system shall support coverage scenarios with up to 16 channels assigned to a frequency. |  |
| VCRF0070 | Alphanumeric Display of Radio Frequencies – On OWP radio frequencies shall be displayed by up to 9 alphanumeric characters, configurable from the Technical Monitoring and Control System (TMCS). |  |
| VCRF0072 | The radio site identification shall be displayed with at least 6 characters. |  |
| VCRF0080 | Frequency Status: - The operational status shall be clearly indicated at the working position. - Out of service / no presence of equipment shall be indicated at the working position. - Equipment failure shall initiate a designated alarm indication and the equipment status shall be indicated in red color until operational again. |  |
| VCRF0084 | Failed or unplugged radio interface card shall not be selectable at the position. |  |
| VCRF0086 | The VCS shall raise an alarm in the TMCS after exceeding predefined time for active PTT at particular frequency channel to prevent accidental occupation of radio channel. |  |
| VCRF0090 | Radio Channel “Out of Service” Indication – If radio channels become unavailable due to maintenance actions on radio units, defective hardware or detected loop check errors an “Out of Service” indication shall be displayed at the appropriately selected channel key for the receiver or transmitter at the operator working position. |  |
| VCRF0100 | Delay compensation – The VCS shall support static delay compensation (adding a fixed delay to a radio channel TX and/or RX). The VCS shall support dynamic delay compensation (relative calculation according to ED-137). Climax delay compensation: The relative delay applied is based in the measured delay values within the frequency coverage, so that minimal delay (<10ms) between first and last TX within the frequency occurs. Receiver delay compensation: The relative delay applied is based in the measured delay values within the frequency coverage, so that minimal delay (<10ms) between first and last RX within the frequency occurs. |  |
| VCRF0110 | Signaling Protocol – The system shall use the SIP (Session Initiation Protocol) as the signaling protocol. |  |
| VCRF0120 | Radio features for complex applications - The system shall support advanced features for safe radio operations in large and complex environments: - Frequency Coupling (transmitting at the same time on more than one radio channel) where it is needed; - Best Signal Selection (BSS) based on digital calculation of audio signal quality integrated in the VCS; - Side-tone Control (local sidetone, remote sidetone, no sidetone). |  |

### Frequency selection

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0130 | It shall be possible to install a frequency at one to five different radio stations, which shall be reflected on the position display. |  |
| VCRF0140 | The operator shall be able to select or deselect any frequency assigned to his position. |  |
| VCRF0150 | By default, frequencies allocated to the position shall be in passive mode (no reception or transmission shall be active at start). |  |
| VCRF0160 | An operator action shall be required to change this mode to receive or transmit modes. |  |
| VCRF0170 | As a result of controller selecting the frequency for receive, transmit or traffic mode, the VCS shall establish connections with the needed radios and presents back to the controller the result of these actions. In case of a missing response from the radio channels (due to radio malfunction or connection failure), the OWP GUI shall inform the controller about the altered state or failure of radio response by user friendly visual means. Following frequency selection states shall be presented to the controller: - Normal frequency state: all selected frequency channels have responded normally and are ready for voice reception/transmission; - Altered frequency state: at least one of the selected channels in any of the coverage groups did not respond normally to the radio call request. In this state, controller is not able to use all radio resources of the frequency for reception/transmission; - Error frequency state: in this situation, none of the selected channels of the frequency responded to the radio call attempts. The controller cannot operate such a frequency. |  |
| VCRF0190 | The controller shall receive a graphical feedback at the OWP HMI of the success or failure of his/her transmission. |  |

### Receive mode

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0200 | This mode shall be selectable on a frequency and site basis, and shall allow for the receiving of the correspondent radio channel at the selected site. |  |
| VCRF0210 | Frequencies selected in receive mode shall be prepared for presenting received audio from this frequency to the operator working position upon detection of squelch. |  |
| VCRF0220 | It shall be possible for an operator to select all frequencies that have been assigned to this operator working position, for the receiving at the same time. |  |
| VCRF0230 | A RX key shall be available and associated with each frequency and site assigned to the position. |  |
| VCRF0240 | Squelch Indication – Squelch shall be visually indicated at all positions having the respective frequency configured. |  |
| VCRF0250 | Pressing the same RX key again shall cease the visual indication that the frequency is in receive mode and stop reception of associated channel at the operator working position. |  |
| VCRF0260 | It shall be possible to configure the system in order to raise an alarm if, for a frequency channel, no RX is selected at least at one position. This requirement shall be configurable per channel. |  |
| VCRF0270 | It shall be possible to configure the system in order to not allow, for a frequency channel, RX deselection at all positions (last position shall not be able to deselect RX). This requirement shall be configurable per channel. |  |
| VCRF0280 | It shall be possible to configure the system in order to not allow, for a frequency channel, RX deselection at any position. This requirement shall be configurable per frequency channel. |  |
| VCRF0290 | Transmission shall not be possible in this mode. |  |

### Receive indication

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0300 | On radio reception, squelch indication of that frequency shall be present at all operating positions having that particular frequency channel selected in RX mode. |  |
| VCRF0310 | For better readability squelch indication shall be extended for a predefined period of time (typically 2 seconds, configurable at TMCS). |  |

### Transmit mode

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0320 | This mode shall be selectable on a frequency and site basis, and shall allow for the transmission on the correspondent radio channel from that position. |  |
| VCRF0330 | Frequencies selected in transmit mode shall be prepared for transmission on activating PTT at the operator working position. |  |
| VCRF0340 | It shall be possible for an operator to select all frequencies that have been assigned to this operator working position, for transmitting at the same time. |  |
| VCRF0350 | A TX key shall be available and associated with each frequency and site assigned to the position. |  |
| VCRF0360 | On activation of the TX key, there shall be a visual indication that the frequency is in transmit mode, and the position shall be connected to the radio transmitter. |  |
| VCRF0370 | If the selected frequency channel was not in receive mode before, selecting TX shall automatically enable receiving on the respective frequency channel. |  |
| VCRF0380 | Pressing the same TX key again shall cease the visual indication that the frequency is in transmit mode and stop connection of associated transmitter to the operator working position. |  |
| VCRF0390 | When more than one radio channel is selected in transmit mode, the operator shall be able to transmit at the same time on all those channels only by pressing the PTT switch. |  |
| VCRF0400 | PTT Pre-emption – It shall be possible to assign pre-emption rights for each position and for each frequency separately. |  |
| VCRF0410 | PTT Active Elsewhere Indication – Active PTT shall be indicated at all operator working positions having the same frequency configured. |  |
| VCRF0420 | Failsafe PTT – The Failsafe PTT feature shall provide a system-controlled PTT timeout. If a PTT signal is active for a configurable time frame at a specific radio channel an alarm shall be generated and displayed on the monitoring OWP. This shall provide continuous access to frequencies, even if frequencies are locked from faulty PTT switches (e.g. from microphones or headsets). |  |
| VCRF0430 | PTT Lockout – The system shall only allow one operator to transmit on any frequency at any time. All additional PTT selections shall be locked out for the duration of the active PTT. |  |
| VCRF0440 | Visual indication of the lock out situation shall be presented at the locked out positions. |  |

### Transmit configuration

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0450 | If more than one site is allocated to a radio channel, it shall be possible to configure that channel for different configurations. |  |

#### Transmitter selection mode

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0460 | A TX key shall be available for each transmitter site where the frequency is available and the user shall manually select transmit mode by selecting any TX key. That selection shall also be the selection of the desired transmitter station. |  |
| VCRF0470 | There shall be a visual indication of the site that is selected for transmission. |  |
| VCRF0480 | It shall be possible to select an alternative transmitter site by pressing the corresponding site TX key. The previously active site key shall be extinguished and a visual indication at the new site key shall be made. |  |
| VCRF0490 | In this mode it shall be possible to select only a single station for transmittion at the same time. |  |
| VCRF0500 | During transmission (active PTT) it shall not be possible to change the selected transmitter station. |  |

#### Multi-station carrier mode (CLIMAX)

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0510 | A TX key shall be available for each transmitter site where the frequency is available and the user shall manually select transmit mode by selecting any TX key. That selection shall automatically select all sites associated with that channel. |  |
| VCRF0520 | There shall be a visual indication of all sites that are selected for transmission. |  |
| VCRF0530 | It shall be possible to de-select a transmitter site by pressing the respective TX key. |  |
| VCRF0540 | On de-selecting of all sites the frequency shall return to receive mode. |  |

### Coupling

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0550 | This function allows the “conference” of frequencies, where a transmission from an aircraft on a particular frequency shall be re-transmitted by all frequencies that have been coupled at the position (duplex patching). |  |
| VCRF0560 | It shall be possible to place at least 4 frequencies in the same coupling group. |  |
| VCRF0570 | It shall be possible to place up to 20 frequencies in the same coupling group. |  |
| VCRF0580 | When PTT is pressed, the operator shall transmit at all frequencies, which have been coupled together. |  |
| VCRF0590 | An operator shall be able to override active PTT generated by an incoming call from the aircraft on any of the frequencies in the coupling group. |  |
| VCRF0600 | There shall be a visual indication at the position that a particular frequency is in coupling mode. |  |
| VCRF0610 | The system shall prevent that a particular frequency is part of two different coupling groups. |  |
| VCRF0620 | If a frequency is in a coupling group at a position and is also available for transmission at other positions, there shall be a visual indication in those other positions that it was placed in coupling mode at another position. |  |

### Best signal selection

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0630 | Best Signal Selection (BSS) shall be available for all channels configured on all sites. |  |
| VCRF0640 | This function shall enable a selection of the best receiver signal out of all selected sites for that channel. |  |
| VCRF0650 | Indication of the selected radio shall be visible at the position. |  |
| VCRF0660 | It shall be possible at a position to override the BSS and for the user to deselect one, two, three or four receiver stations out of the maximum five. The visual indication of the deselected sites shall be extinguished. |  |
| VCRF0670 | The BSS shall occur only between the stations that are RX selected by the user. |  |
| VCRF0680 | User initiated configuration changes at a position shall not change the configuration of that frequency at other positions. |  |
| VCRF0690 | BSS shall be performed automatically by evaluation of the radio signal quality by the system (full BSS function). |  |
| VCRF0700 | The Tenderer shall describe the method for performing BSS, the timings considered and shall refer the cases where there is signal degradation during use of channel. |  |
| VCRF0710 | During the evaluation period of the BSS, the VCS shall always provide an incoming audio signal to the operator active audio devices. |  |
| VCRF0720 | For channels configured for BSS and not working in offset mode, the following modes of transmitting selection shall be possible during the BSS operation (it shall be possible to define this configuration at the TMCS). |  |

#### Site transmitter follows BSS

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0730 | If this configuration is activated for a channel, there shall be an automatic selection of the transmitter within a group. That selection shall be the result of the last site selection for best signal at the BSS. |  |
| VCRF0740 | The selection of the TX site shall take place anytime when there is a reception and BSS occurs. |  |
| VCRF0750 | It shall be impossible to switch transmitter site during active transmission at that channel. |  |
| VCRF0760 | The automatic selection shall be able to be overridden by the operator at any time. |  |
| VCRF0770 | In this mode it should be possible to define, as needed, a default transmitter site to be automatically selected after certain period of time without any activity on the channel (on a frequency basis). |  |

#### Site transmitter selected by the operator

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0780 | If this is the configuration for the channel, only the operator shall be able to select transmit site for that channel. |  |

### Sidetone

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRF0790 | The system shall provide three possibilities for generating sidetone (operator’s transmit audio received at his position): Remote Sidetone: No sidetone shall be generated within the system. The system shall not block the reception coming from the radio interface (sidetone from RX). Local Sidetone: On PTT activation, a local sidetone shall be generated inside the system and routed to the position receiving device. No Sidetone: On PTT activation, no reception on the same channel shall be available on the transmitting position. |  |
| VCRF0800 | It shall be possible to configure remote, local or no sidetone on a per role basis. |  |

## TMCS

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0010 | The system shall be provided with a Technical Monitoring and Control System (TMCS), allowing for the technical and operational control of the VCS, logging of all relevant system events and collection of data for statistical purposes. |  |
| VCTM0020 | The TMCS shall provide the management of system configuration parameters and of system software. |  |
| VCTM0030 | The TMCS shall be able to perform configuration of operator working positions and telephone and radio interfaces. |  |
| VCTM0040 | The TMCS shall allow loading of different system configurations and performing of all on-line reconfigurations of the system in a quick and easy way. |  |
| VCTM0050 | All system configuration and pre-configuration parameters shall be possible to be recorded on a safe storage media. |  |
| VCTM0060 | All system software packages should be able to be downloaded from the TMCS. |  |
| VCTM0070 | The TMCS shall be able to download the layouts for the position panel. |  |
| VCTM0080 | The TMCS shall allow automatic monitoring of main system components, including external interfaces, power supplies and positions. |  |
| VCTM0090 | The TMCS shall be able to perform fault diagnosis and to display system status up to board level. |  |
| VCTM0100 | The TMCS shall perform the recording of all relevant system events. |  |
| VCTM0110 | At the TMCS it shall be possible to perform statistical data collection. |  |
| VCTM0120 | The TMCS shall not be required for normal operation of the VCS. |  |
| VCTM0130 | The TMCS shall have redundant connection to the VCS. |  |
| VCTM0140 | The TMCS access shall be multilevel password protected to enable multi-user operation. |  |
| VCTM0150 | Several degrees/levels of access and priority shall be possible for the TMCS functions, including an access level with no editing or modification are allowed. |  |
| VCTM0160 | An access level shall exist that allows only the allocation of operational maps (roles to physical positions). |  |
| VCTM0170 | It shall be possible to assign positions, TMCS profiles and configurations to an operational group (up to 5 different groups). |  |
| VCTM0180 | On operational map assignment performed from a TMCS profile belonging to a specific group shall consider only positions, roles and configurations defined as accessible for that group. |  |
| VCTM0190 | A global TMCS operational profile shall allow operational assignment and configuration for all defined operational groups. |  |
| VCTM0210 | The TMCS clients shall be able to display permanently the system status via a graphical user interface. |  |
| VCTM0220 | The full software package necessary to operate those clients shall be delivered. |  |

### System configuration

#### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0230 | The configuration function of the VCS shall provide authorized operators with the capability to reconfigure positions and system parameters. |  |
| VCTM0240 | The main possible configurations shall regard the addition of new equipment’s and the definition of single positions roles and global position maps. |  |

#### Global configuration

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0250 | The configuration function shall validate the changes in the configuration (e.g. check consistency) and provide feedback for the user. |  |
| VCTM0260 | Different configuration versions shall be available for selection and activation in the system. |  |
| VCTM0270 | The system shall allow to make manual backups of the whole configuration. A unique version reference including date and time shall be provided with each backup. |  |

#### Position configuration

The role represents a set of functions and access to telephone lines and radio channels, which enable operator to perform different specific tasks. It defines an operator working position without definition of physical allocation.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0340 | At least the following roles parameters shall be configurable by means of TMCS: - Role names, - Call-out numbers / identification; - ATS number identification (independently per DA); - Routing of incoming calls towards the role; - Access to radio and telephone lines; - DA layouts. |  |
| VCTM0350 | It shall be possible to change roles from TMCS. |  |
| VCTM0360 | To avoid loss of communication, the new role should only be active when the operator presses a confirmation key, until then the old role shall remain active. |  |

### Monitoring functions

#### Current status

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0370 | Through the TMCS it shall be possible to display information about the current configuration and status. |  |
| VCTM0380 | It shall be possible to display the following information about the current status: - Activated roles at all positions; - Activated global configuration; - Status of positions (active, diverted, out of service); - Active alarms; - All equipment’s status; - ATS number allocation. |  |
| VCTM0390 | A graphical user interface of the TMCS shall indicate the system failures or degradation at replaceable module level. |  |

#### History file

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0400 | To allow the tracking of events on the system a past history file(s) shall be delivered as part of the TMCS package. |  |
| VCTM0410 | History file shall maintain a record of all events reported in the system. |  |
| VCTM0420 | History file(s) shall contain: - Logins and logouts of TMCS users; - Changes in current status; - Configuration changes performed from TMCS by users; - Telephone calls (caller and called party, time and date, duration); - Activated telephone functions at positions; - Radio communications (channel and frequency, position, time and date, duration); - Activated radio functions at positions. |  |
| VCTM0430 | Existing limits for the size of the history file shall be indicated. |  |
| VCTM0440 | Supplied TMCS client shall include a suitable unit for storage of at least 30 days of the history file. |  |
| VCTM0450 | For further analysis it shall be possible to export data from history file or any filtered part of it to a standard industry format (e.g. xls, doc, pdf, txt, csv). |  |
| VCTM0460 | In order to allow a future integration of recorded data from the VCS and other systems, the history file shall be timestamped. |  |

#### Diagnostics

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0470 | The correct functioning of the system shall be supervised from the TMCS. |  |
| VCTM0480 | The system shall run continuous diagnostic checks, including periodical check procedures on units that don’t work in continuous operation. |  |
| VCTM0490 | In case a failure is found, the VCS system shall be able to provide detailed information about the failure. |  |
| VCTM0510 | Diagnostics shall be able to trace a failure up to printed circuit board level. |  |
| VCTM0520 | The failure message shall contain at least: - Date and time of failure; - Severity level of failure; - Equipment involved in failure. |  |

#### Alarm file

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0530 | For the tracking of failures in the system a past alarm file(s) shall be delivered as part of the TMCS package. |  |
| VCTM0540 | Alarm file(s) shall contain: - All resolved and still active error messages; - All error and warning messages; - Time of failure; - Type of failure; - Equipment involved in failure. |  |
| VCTM0560 | Supplied TMCS shall include a suitable unit for storage of at least 30 days of the alarm file. |  |
| VCTM0570 | For further analysis it shall be possible to export data from alarm file or any filtered part of it to a standard industry format (e.g. xls, doc, pdf, txt, csv). |  |

### Statistics

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0580 | The system shall be provided with a statistical package. |  |
| VCTM0590 | This facility shall control the acquisition, storage and processing of statistical data. |  |
| VCTM0600 | It shall be possible to collect the following information from the VCS: Traffic information - Address information (originator and destination address); - Call result; - Line/trunk used; - Frequency activity; - Telephone line activity; The processed information shall - Be stored for at least 30 days; - Be exported the traffic analysis data into a standard format (e.g. xls, doc, pdf, txt, csv). |  |

### SNMP output

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTM0610 | The TMCS shall allow integration in Slovenia Control’s dedicated supervisory system. |  |
| VCTM0620 | For this purpose it shall provide a SNMP output interface using version v2c of SNMP protocol. All functions defined for this protocol version shall be available. |  |
| VCTM0630 | System state information and its major components shall be delivered using a trapping mechanism (on occurrence of an event a trap is sent) and maintained through a polling mechanism (answering snmpget requests). |  |
| VCTM0640 | System information shall be hierarchally organized and shall be presented under a MIB (Management Information Base) form, which shall include the definition of all essential parameters of the system, as well as the definition for trap messages. |  |
| VCTM0650 | Definition of the complete message structure shall be agreed at a later phase, through the establishment of an ICD. |  |
| VCTM0660 | The configuration of SNMP manager, like the address and port number of trap destination shall be possible, and it shall also be possible to configure SNMP write and read communities. |  |

## Roles, Missions and Re-configuration of Sectorization

### Roles

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRM0010 | The system shall support the concept of roles. A Role represent a certain operational task or responsibility within the operation of the airspace. The role is defined by at least: - Role name; - An identity (unique MFC-R2/VoIP/PSTN number) under which the role can be contacted; - Radio Frequency keys; - Telephony keys; - Radio and telephony keys layout; - Permissions to access functions (e.g. Cross Coupling activation, frequency change, Tx selection, etc.) - A Default chime – at least 9 variants. |  |
| VCRM0020 | A defined period shall be configurable before a position goes into unattended state after the last microphone, handset or headset has been disconnected from its socket. In unattended state all radios are keyed out automatically. |  |
| VCRM0030 | Each role shall be assigned with a set of A/G and/or G/G keys as configured in the TMCS management system. |  |
| VCRM0040 | The VCS role concept shall support dynamic sector management (e.g. merging of sectors during operation). |  |
| VCRM0050 | The VCS role concept shall support the following role handling mechanisms: - Static role to controller allocation; - Dynamic role handover between controllers during operation; - Selection of roles from each OWP regardless of the number of other controllers with the same role. |  |
| VCRM0060 | The VCS shall have a prevention mechanism to ensure that there are no unassigned roles. The prevention mechanism shall be able to be activated/deactivated from the TMCS. When the prevention mechanism is activated, a role shall be assigned to at least one OWP. |  |
| VCRM0062 | In order to cover the various tasks of an operator depending on his assigned role, the VCS shall allow to configure an HMI layout per role. |  |
| VCRM0064 | The TMCS shall allow to assign default frequencies to a role. |  |

### Missions

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRM0070 | A mission shall be created by assigning one or more roles to the mission. |  |
| VCRM0080 | All settings of the mission shall be inherited by taking the settings of the top (main) / first role part of the mission. |  |
| VCRM0092 | It shall be possible to assign up to 20 roles for each mission. |  |
| VCRM0094 | For each mission it shall be possible to assign a prioritary role to be used for the origin identity and presented layout. |  |

### Functional Requirements

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRM0100 | The operator shall be able to change the configuration of the working position when new configurations are available. |  |
| VCRM0110 | Mission changes should be manually confirmed at any affected operator working position without time limitation. |  |
| VCRM0120 | The previous operator working position mission scenario should be operational until new mission confirmation. |  |
| VCRM0130 | The system shall recognise unattended operator working position if there are no devices (microphone, handset or headset) connected to the OWP. |  |
| VCRM0140 | The technical monitoring and control system shall have multilevel password protection. |  |
| VCRM0150 | Each operational function shall be activated either by pressing dedicated function key or typing a function code. |  |
| VCRM0160 | It shall be possible to define scenarios within the VCS system. A scenario can allow a predefined combination of missions to be used on operator positions. |  |
| VCRM0170 | The activation of a scenario should be possible via the supervisor view and effectively makes the missions usable at the affected operator positions. |  |

## Operator Working Position

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0010 | OWP positions shall consist of: - 12” capacitive touch screen computing unit (Solutions where the touch screen and the OWP processing unit are separate equipment are also accepted.); - Audio boxes with sockets used for connecting all audio periphery; - Loudspeakers. |  |
| VCWP0020 | All operator working positions shall be identical in regards of telephone and radio functionalities. |  |
| VCWP0030 | The OWP shall have duplicated network and power supply connections and shall be able to supply the power for the display unit. |  |
| VCWP0040 | The touch screen computing unit and the audio box shall be configured without fans (no active cooling) to avoid unnecessary noises at the position. |  |

### Operator panel

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0050 | The panels shall be state of the art technology. |  |
| VCWP0060 | The hardware concept of the panel shall be based on commercial of the shelf (COTS). |  |
| VCWP0070 | Each operator working position shall be equipped with one functional panel to manage the operational functions of the system. |  |
| VCWP0080 | Panels can be operated for radio, telephone or in a mixed mode. |  |
| VCWP0082 | One part of the panel screen shall be dedicated to the frequencies and one part of the screen to the telephone to avoid the implementation of an additional screen. |  |
| VCWP0090 | The operator working position panel shall be of a versatile design and performance to allow operation in ATC environment and be ready for future modifications. |  |
| VCWP0100 | The operator panel shall be Touch Entry Device (TED). |  |
| VCWP0110 | The TED shall have dimensions of 12” in diagonal. For installation purposes, the supplier will provide appropriate mechanical interfaces for the TEDs to be installed in the controller consoles. |  |
| VCWP0112 | A bright, professional TED with at least 1000 Cd/m2 shall be used. |  |
| VCWP0120 | The TED shall have redundant network connection and shall have at least the following specifications: - High Contrast, Anti-Glare, TFT-LCD-display; - Resolution 1024 x 768, Wide Viewing Angle; - Capacitive Touch, reaction time <15 ms; - Designed for 24h/7d ATM Grade Operation; - Fanless; - LED backlight; - Console and VESA mounting possibilities. |  |
| VCWP0122 | The normal life cycle of the TED including the backlight shall be at least 44.000 hours (5 years), running with full brightness. |  |
| VCWP0124 | The TEDs shall operate without forced cooling. |  |
| VCWP0130 | The TED panel shall give a clear indication of all the facilities selected by the operator. |  |
| VCWP0150 | The size of the keys shall be determined by the requirement of easy access and clear identification. A size in the order of 20x20 mm shall be taken into consideration. |  |
| VCWP0170 | The screen shall be a multi touch and accurate when used. Direct sunlight or artificial light shall not completely obscure the content of the screen. |  |
| VCWP0180 | The display shall provide viewing angle of minimum 120º (both horizontal and vertical) taking into account the different locations of installation in the working positions. |  |
| VCWP0190 | It shall be possible to perform audio device test or diagnostic at the operator working position. |  |

### Panel layout

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0200 | The layout shall contain telephone pages, radio pages and mixed telephone and radio pages. |  |
| VCWP0202 | The system shall support the ability to choose between telephone or frequency centred layout. |  |
| VCWP0210 | To provide the user with access to all DA keys, the layout shall allow the utilization of pages. It shall be possible to select any page by means of page tag or by pressing the appropriate key. |  |
| VCWP0220 | The most important information shall be always visible and shall not be covered when changing the selected page. |  |
| VCWP0230 | Function keys shall be designed so that different functions are easily distinguishable. |  |
| VCWP0240 | The contents of the layout keys (telephone keys, frequency keys and function keys) shall be assigned from the TMCS. |  |
| VCWP0242 | Rapid UI – A VCS Software-toolbox for quick prototyping and configuration of specific user layouts for touch entry devices shall be available in the overall TMCS. |  |
| VCWP0244 | It should possible to present at the OWP HMI the video streams received from IP cameras. |  |
| VCWP0246 | The OWPs should be able to present to the controllers text feeds (e.g. reads from HTTP server). |  |

### User devices

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0250 | Each OWP position shall be able to support 2 OP/CO device sockets for microphones, handsets and headsets – 4 sockets in total, type LEMO-connector. |  |
| VCWP0260 | The flexibility in the use of sockets for the different audio devices shall be considered. |  |

#### Handset

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0270 | A handset shall be delivered for each operator working position. |  |
| VCWP0280 | The handsets shall be professional and of high quality, lightweight but robust enough to sustain the normal handling during its usage and provide a high degree of reliability during its operational life. |  |
| VCWP0290 | Handset cradles shall be provided at all positions. |  |
| VCWP0300 | The handset shall be provided with a spiral cable of up to two metres of length (when extended). |  |

#### Loudspeaker

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0310 | Each OWP position shall be able to support one loudspeaker. |  |

#### Microphone

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0320 | All microphones shall be dynamic and fitted with noise cancelling mechanisms. |  |
| VCWP0330 | All microphones shall be built robustly to sustain constant air traffic control use. |  |

### Volume control

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0340 | The position shall allow following volume controls: - Independent volume control for the connected headset for the instructor and operator; - Volume control for the handset; - Volume control for the loudspeaker. |  |
| VCWP0342 | Output levels shall be adjustable over a range of about 30 dB without detriment to the audio quality. |  |
| VCWP0350 | In the case of the headset and the handset this control shall be available at the panel layout. |  |
| VCWP0360 | In the case of the loudspeaker this control shall be available at the layout or at the module itself. |  |
| VCWP0370 | In the case of headset use, there shall be a pre-established maximum audio level. This maximum level shall be configurable at the TMCS. |  |
| VCWP0380 | For all volume controls the minimum level shall be set in a way to prevent complete cut-off. This minimum level shall be configurable at the TMCS. |  |
| VCWP0390 | It shall be possible to adjust separately volume level for telephone and for radio communications. |  |
| VCWP0400 | It shall be possible to adjust volume for each assigned frequency per panel individually. |  |

### Audio routing and device selection

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0410 | Active audio shall be routed based on the type of communication, used audio device, selected audio functions and applied audio routing mode. |  |
| VCWP0420 | Microphone shall be used primary only for radio communications. |  |
| VCWP0430 | For radio audio reception the operator shall have the possibility to select for each channel separately loudspeaker, headset or both. |  |
| VCWP0432 | Headset/Loudspeaker Selection for A/G and G/G Communications – These functions shall allow the operator to select for all incoming A/G and G/G calls in common, whether incoming voice is presented in the headset or at the handset and loudspeaker. If using a headset, it shall be possible to select simultaneously listening of the frequency by the loudspeaker. |  |
| VCWP0440 | Default radio receiver audio device shall be loudspeaker. |  |
| VCWP0450 | There shall be a unique visual indication of the active audio devices. |  |
| VCWP0452 | All audio devices shall incorporate an appropriate level of EMC protection. |  |

### Sockets

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0460 | Socket for handset and headset shall allow an easy handling in terms of orientation of the plugs. |  |
| VCWP0462 | Sockets shall be separated from the TED and properly positioned for right-handed and left-handed operators. |  |
| VCWP0470 | 2 sockets shall be positioned on the left side of the TED, 2 sockets shall be positioned on the right side of the TED at the operator working position. |  |
| VCWP0480 | Sockets shall allow operation of coach/trainee function as described in Training on operator working position section. |  |

### Split headset

This section describes specifications for the audio routing for dedicated outputs available at the sockets.

#### Audio Routing

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0490 | The VCS shall provide the following setting options for A/G audio routing to output devices (loudspeakers, headsets, etc.): - TCMS settings (as default/general audio routing); - Locally configured audio routing for each working position level; - Per frequency audio routing (for each individual frequency). |  |
| VCWP0500 | Radio audio shall be routed to the following audio outputs according to the configuration per each frequency: - At the left and/or right audio channel of the stereo headsets; - At any combination of loudspeakers. |  |
| VCWP0510 | In addition to headset/handset/microphone volume settings at each OWP, a per-frequency volume setting shall be provided at the OWP GUI to the controller. Controllers shall be able to adjust individually the volume of the voice received from each frequency. The frequency volume level shall be adjusted in relation to the volume level of the output audio device to where the audio is routed. |  |
| VCWP0520 | Telephony audio shall be routed to the following audio outputs: - At the left and/or right audio channel of the stereo headsets; - At any combination of the loudspeakers. |  |

#### Audio Control

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0530 | The OWP shall be able to automatically detect the connected audio accessories (handset/headset, microphone) and adjust the dynamic parameters accordingly. The presence/absence of the connected audio accessories shall be indicated in the HMI. |  |
| VCWP0540 | The audio volume for headsets/handsets and loudspeakers shall be individually adjustable from the OWP HMI or from the physical knob at the front panel of the audio modules. |  |
| VCWP0550 | The audio module for connecting loudspeakers or the loudspeaker itself shall have a visual indication on the front panel that indicates audio activity for each of the loudspeakers. |  |

### Audio indication

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0560 | On the radio page there shall be a visual indication of existing speech – relevant radio channel is transmitting or receiving communication from an aircraft. |  |

### Panel controls

#### Brightness control

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0570 | A brightness control shall be provided at all TEDs. |  |
| VCWP0572 | The brightness of the screen shall be adjustable, and the user shall be able to change by himself. |  |
| VCWP0580 | A test of all indication elements shall be available. |  |
| VCWP0590 | The screen brightness shall be up to 1000 Cd/m2. |  |
| VCWP0594 | The TED shall have a screen saver function when not in use. |  |

#### Chime

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0600 | A chime to announce incoming telephone calls shall be integrated into the panel. |  |
| VCWP0610 | The chime shall operate with several modes and different chime (ringing) tones. |  |
| VCWP0620 | The following controls shall be available: - Chime mode selection; - Chime volume control; - Chime on and off switch. |  |
| VCWP0630 | The Chime Volume Control function shall enable the operator to adjust the volume of the acoustic signal issued by TED when a call comes in. |  |

#### Cleaning mode

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0640 | In order to allow regular cleaning of the panel, it shall be possible to deactivate (freeze) keys on the display. There shall be a visual indication of the freezing state of the panel. |  |

### Training on operator working position

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0650 | Training shall be possible at all positions, by means of establishing defferent socket priorities. |  |
| VCWP0660 | Socket for the coach microphone or headset shall have higher priority than socket for the trainee microphone or headset. |  |
| VCWP0670 | If only one microphone or headset is connected at the position, radio transmit shall be possible and operate normally for coach or for trainee socket. |  |
| VCWP0680 | If both sockets are connected at the same time, both microphones or headsets will be active for transmitting, but when both PTT switches are pressed at the same time, the coach’s PTT will override the trainee – transmission shall only be possible for the coach. |  |
| VCWP0690 | There shall be no prioritisation between a coach socket in a position and a trainee socket at another position. |  |
| VCWP0700 | Socket shall have a visual and clear indication of which is intended for coach and which is intended for trainee. |  |
| VCWP0710 | The footswitch PTT will work in parallel with the PTT switch on the trainee microphone or headset. |  |

### HMI design and interaction

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0720 | All essential resources and functions shall be available on the main screen and shall be activated by simple touch actions. The HMI shall be designed to allow one-touch operation for frequently used function: - Activation / deactivation of radio and telephone functions; - Opening of secondary windows (audio settings and routing, frequency configuration mode); - Closing menus or additional windows to return to the main screen. |  |
| VCWP0730 | Essential operational information, such as the incoming telephony queue, alerts and messages shall be always visible. |  |
| VCWP0740 | The design of the HMI regarding key-sizing and key-placement shall be fully and flexible for radio keys, DA keys and function keys. Size of the call queue shall be flexible. |  |
| VCWP0750 | The colour of the DA keys shall be configurable, selectable from at least 20 colours. |  |

### Short Term Recording

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0760 | The system shall provide short term recording for recording and playback of recent incoming or outgoing telephone and radio calls on an operator working position. |  |
| VCWP0770 | Short term recording shall be provided for active calls on the operator working position with a maximum storage capacity of 60 minutes of actual voice. |  |
| VCWP0780 | If there is an active radio call and a telephone call at the same time, both calls shall be recorded. |  |
| VCWP0790 | Reception of a radio call shall interrupt playback of short term recording. |  |
| VCWP0800 | Operation of playback function shall not interrupt the short term recording. |  |
| VCWP0810 | If the allocated memory for short term recording is consumed, the first (oldest) recorded call shall be overwritten. |  |
| VCWP0820 | For the purpose of playback at least the following information shall be available on the recording list: - Time stamp for the communication; - Type of communication (radio or telephone); - Telephone correspondent or radio channel identification. |  |
| VCWP0830 | It should be possible for a privileged position or TMCS client to playback recordings from any other position. |  |
| VCWP0840 | Repetition of the last radio sentence at a position shall be allowed, using special function key – “Say again” key. |  |

### Position unattended

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCWP0920 | The system shall prevent to establish an active telephone or radio communications at positions in unattended mode (no audio devices connected). |  |
| VCWP0930 | In unattended mode the radio reception shall be routed to loudspeakers, independently of the selection set on the panel. |  |

## Legal recording

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCLR0010 | All outgoing and incoming operational speech shall be passed to the recording interface to allow the legal recording of all voice activities. |  |
| VCLR0020 | The VCS shall be able to interconnect to analogue and VoIP based recorders. |  |
| VCLR0030 | An analogue recording output circuit shall be included for each analogue line interface, for both A/G and G/G, which combines the transmitted and received audio signals. |  |
| VCLR0040 | To enable a redundant, independent recording each operator position shall be equipped with two independent recording outputs which can be connected to two independent recording systems. |  |
| VCLR0050 | The VCS shall be able to provide, for recording purposes, all operator panel communication (all A/G and all G/G communication). |  |
| VCLR0060 | The VCS shall provide VoIP recording interfaces according to ED-137 for recording of each OWP and external radio/telephone interface (both analogue and IP). |  |

## Interface Specifications

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0010 | The VCS shall provide a comprehensive range of functions for radio, telephone and intercom. |  |
| VCIS0020 | Every feature and operational function shall be separately enabled or disabled and shall be configured by software parameters to allow easy adaptation to specific requirements. |  |
| VCIS0030 | All interface levels shall be software configurable from the technical monitoring and control system (TMCS). |  |
| VCIS0040 | For safety reasons each physical equipment (radio equipment, phone lines, servers, OWPs ...) shall be connected redundantly to the network. |  |
| VCIS0050 | A simple and “hot” replacement of interfaces shall be possible without a shutdown of the system – each changed interface shall support an automatic reset and self-configuration without manual adjustments. |  |
| VCIS0060 | Each legacy radio and telephone interface shall provide a recording output for summed audio of incoming and outgoing speech. These recording outputs shall be able to be connected to a multi-channel recorder for legal channel/line recording. |  |
| VCIS0070 | All analogue audio interfaces (telephone and radio) shall have a nominal impedance of 600 Ω balanced. |  |

### Network capabilities – open standard interconnection

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0080 | The VCS shall have the possibility to be integrated into any ATC network via various transmission media such as MFC, ATS-QSIG or ED137 G/G connections. |  |

### Telephone interfaces

#### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0090 | The system shall support a number of interface modules providing interconnection with both analogue and digital networks: - 4-wire analogue telephone interfaces (e.g. MFC-R2 according to EUROCONTROL). - digital interfaces ATS-QSIG 64 kbit/s. |  |
| VCIS0100 | The line interfaces required between the network and the communication system shall be compatible with the ITU-T regulations for leased circuits in particular with respect to signal level, speech level and impedance. |  |
| VCIS0110 | Configuration and status monitoring of all interfaces shall be performed from the TMCS. |  |
| VCIS0120 | The offer shall include values of input and output signal levels for each analogue interface. |  |

#### Audible tones

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0130 | In addition to the visual indications the system shall provide audible tones at OWPs. |  |

##### Ring-back tone

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0150 | After call set-up and prior to the acceptance of the call by the called terminal a ring-back tone shall be sent to the calling terminal. |  |
| VCIS0160 | The ring-back tone shall consist of a sequence of 1 second 425 Hz tone and 4 seconds of silence. |  |

##### Interrupt warning tone

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0170 | If an established call is subject to a priority interruption, the parties concerned shall be warned of the imminent interruption. For this purpose an interrupt warning tone shall be generated and heard for some seconds. |  |
| VCIS0180 | The warning tone employed shall have a frequency of 1000 Hz. The warning tone sequence shall consist of tone duration of 40 ms followed by 1 second of silence. |  |

##### Terminal busy tone

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0190 | If a terminal is busy (the call cannot be delivered to the terminal), the line to the calling exchange shall be released and the calling terminal shall receive a busy tone from its own system. |  |
| VCIS0200 | The busy tone shall consist of 170 ms tone of a frequency 450 Hz followed by 170 ms of silence. |  |

##### Unserviceable tone

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0210 | If a called terminal is out of service, not available or the number dialled is not allocated, a special tone shall be heard by the calling terminal. The line shall be released and the calling exchange shall provide the appropriate tone. |  |
| VCIS0220 | The unserviceable tone shall consist of 500 ms tone of a frequency of 1000 Hz followed by 500 ms of silence. |  |

#### Interface types

##### FXS interface

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0250 | The VCS shall support a FXS interface that allows connection to a standard telephone. |  |
| VCIS0260 | The FXS interface shall allow the configuration of a standard telephone and connection to a FXS voice interface card. |  |

##### PSTN and PABX line interface

This interface provides an analogue connection to the public switched telephone network (PSTN) directly or via a PABX.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0270 | The interface shall receive signalling from a central office of the PSTN. The PSTN interface shall provide the following primary service to the Telco network device: on-hook/off-hook indication (loop closure). |  |
| VCIS0280 | It shall be possible for dialling to use DTMF signalling. |  |
| VCIS0290 | It shall be possible to utilize the same interface type to connect either an analogue PSTN line or an analogue PABX extension line. |  |

##### MFC line interface

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0300 | This interface shall be used to interconnect the system with MFC operated circuits – leased 4-wire voice lines. The line interface unit shall take care of all necessary signalling towards the line as generation and detection of signalling tones and signalling control. |  |
| VCIS0310 | This interface shall be compliant with specification of MFC-R2 signalling procedure given in EUROCONTROL “ATS R2 and ATS No.5 protocol specification Ed 2.0” from 22nd of February 2005. |  |
| VCIS0320 | For each MFC-R2 or No.5 line connected to a VCS it shall be possible to configure from the TMCS the VCS to be the “A” side or the “B” side for call processing purposes. |  |
| VCIS0330 | The VCS shall support a 4-wire interface that allows connection to a four wire circuit conforming to ITU-T G.712 |  |

##### QSIG line interface

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0340 | The VCS system shall be equipped with digital telephony interfaces or gateways for ATS-QSIG communication. |  |

##### Primary ISDN line interface

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0380 | Primary ISDN interfaces shall enable connection to the PSTN or to local PABX. |  |
| VCIS0390 | The physical and electrical characteristics of the interface shall conform to EURO ISDN standard. |  |

##### ATS-SIP VoIP interface

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0400 | ATS-SIP VoIP interface and protocol shall be in line with EUROCAE ED-137B/C (VoIP). |  |
| VCIS0401 | The VCS should offer IP PABX functionalities to the VCS telephony users. |  |
| VCIS0402 | The VCS should support the following telephony functions for the VCS telephony users: - Basic Calls; - Call hold/music on hold; - Call forward; - Voicemail – incoming calls are re-routed to the voicemail service aloowing the calling party to leave an audio message; Vocemail can be configured from the VCMS; - Call transfer; - Conferencing; - Call hunting; - Call forking; - Call pick-up; - Do not disturb (DND) – this feature shall allow the VoIP SIP phones users to reject all incoming calls by generating a “Busy” release clause; - Anonymous call rejection – this feature shall allow a VoIP SIP phone to reject all incoming calls with no caller ID or the privacy attribute enabled; - Calling line identification presentation (CLIP); - Calling line identification restriction (CLIR) – when activated, it shall allow all the outgoing calls from a VoIP SIP phone to be placed with an anonymous caller ID number. |  |
| VCIS0403 | The VCS telephony users should be able to place and receive calls using VoIP SIP hard phones. |  |
| VCIS0404 | Configuration and management of the VCS telephony users should be performed from the VCS management system. The individual VoIP SIP hard phones shall be configured from their own web interface. |  |

### Radio interfaces

#### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0410 | The system shall support both 4-wire and VoIP radio interfaces simultaneously. |  |
| VCIS0420 | Both types shall allow configuration to work either with PTT/squelch or vox (voice operated reception) modes. |  |
| VCIS0440 | Network connection to the remote radio sites shall be redundant. |  |

#### Interface types

##### 4-wire

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0470 | The VCS shall support a 4-wire interface that allows connection to circuits conforming to ITU-T G.712 |  |

##### VoIP interface

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCIS0500 | VoIP interface and protocol shall be in line with EUROCAE ED-137B/C (VoIP). |  |

### 3rd party systems interfaces (external systems)

This chapter describes the required actions and data for interface needs to 3rd party systems (external ATM systems, not VCS) for future implementation of interoperability functions.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCEX0010 | VCS shall provide open interface to receive, send and execute required actions and data to external systems. |  |
| VCEX0020 | It shall be possible to connect VCS to external systems via LAN. |  |
| VCEX0030 | VCS shall from external system receive and execute commands: - the start of call; - end of call. |  |
| VCEX0040 | VCS shall send to the external system data that call is: - waiting to be answered (call is waiting to be answered – is ringing); - call is in progress; - call is terminated; - not possible to establish connection to called number (number is busy, line is not available). |  |
| VCEX0050 | It shall be possible to add commands and data that are send to external systems to the VCS in later time. |  |
| VCEX0060 | In case that the call is initiated from external system identification to the called party shall be the same as the call was initiated from the VCS panel. |  |
| VCEX0070 | Call initiated from the external system shall be by VCS treated the same as it would be initiated from VCS panel. Remark: End of call, conference call, indication of the call on the VCS panel, possibility to end call on the VCS panel. |  |
| VCEX0080 | VCS shall be able to establish connection with any allowed number received from external system. |  |
| VCEX0090 | VCS and external system should exchange heart bits. |  |
| VCEX0100 | In case that heart bits are not received for defined period of time alarm should triggered on appropriate working position (MIB). |  |
| VCEX0110 | The tenderer shall describe type of connection, type of component which is interfaced and description of used protocols for external systems. |  |
| VCEX0120 | Format of messages shall be agreed between both parties. |  |

## Transit

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCTR0010 | The system shall have the ability to route an incoming call from another VCS (preceding VCS) via an external interface to another VCS (subsequent VCS). The manner in which individual calls are processed is dependent on the signalling utilized on the incoming and outgoing external interfaces of the transit VCS. |  |

## System timing

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCST0010 | The system shall have an internal clock which shall be capable of being synchronized by an external source. |  |
| VCST0012 | In case that no external source is available, system timing shall be provided by the internal clock source. |  |
| VCST0014 | For the purpose of the logging all events and status of the VCS, TMCS shall have the means to be synchronized by an external source – NTP server to be supplied by Slovenia Control. |  |
| VCST0020 | PTT Selection Timing – The delay from pressing PTT at the position to closure of the contact at the radio interface shall be of less than 80 ms in 99%. |  |
| VCST0030 | Call Connection Setup Time – The Call Connection Setup Time shall be within 1 second or less in 99% of the time for IA/OVR calls and less than 2 seconds for any other G/G call. |  |
| VCST0040 | Main/Standby Transfer Time – The system shall require less than 600 ms in 99 % to generate M/S transfer signal measured from the instant that the M/S TX/RX selector is engaged until the transfer signal is present at the Air/Ground interface. |  |
| VCST0050 | VCS start-up time – The VCS shall not require more than 7 minutes for start-up. |  |
| VCST0060 | Requirements for all timing and delay parameters not demanded in this document shall be in line with EUROCAE ED-137B/C (VoIP). |  |

## RAM (Reliability, Availability, Maintainability)

### General

Reliability, Maintainability and Availability are characteristics of the overall system which shall be specified, designed, implemented, tested, validated and documented. The quality of equipment can be considered as its ability to satisfy the user needs for the specified period of time and can be expressed with its operational availability. Two major contributors to the quality are: - Reliability, and - Maintainability.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRG0010 | The methodology, techniques, processes and tools the Tenderer intends to use to achieve the specified RAM objectives shall be described or referenced in specific plans addressing architecture, hardware and software aspects. |  |
| VCRG0020 | All central components shall be redundant – servers, interface controller boards etc. |  |
| VCRG0030 | The working position shall be connected via two independent LAN segments. |  |
| VCRG0040 | Each Working Position shall have two independent IP addresses (which are not part of the same subnetwork) to reach full independence of single LAN outages. |  |
| VCRG0050 | Operator Working Position Air/Ground Audio shall be distributed in parallel over the two LAN segments (no hot standby switchover). |  |
| VCRG0060 | Failures within the VCS shall automatically be detected and identified using online diagnostic software. |  |

### Reliability

Reliability is defined as a probability that equipment will perform its intended function without error, under stated conditions, for a specified period of time.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRR0010 | The Tenderer shall provide in the tender documentation a reliability model consisting of reliability block diagrams covering all functions of the system. |  |
| VCRR0020 | The MTBF and MTTR in hours and the availability shall be clearly shown in either a block diagram or a list showing the equipment breakdown to the functional unit level, with the identification of a specific common failure mode (e.g. switch over equipment). |  |
| VCRR0030 | The Tenderer shall provide in the tender documentation reliability predictions and analysis as per standard MIL-HDBK-217 or other commonly used and accepted method which shall be clearly stated. |  |
| VCRR0040 | As the VCS is a critical equipment, it shall have a very high reliability. The failure of any single component shall mean, at most, the loss of only one interface card, or one operator working position. A single failure within all other system parts shall not affect normal operation of the VCS. |  |

### Maintainability

Maintainability is the measure of the ability of an item to be retained in or restored to a specified condition when maintenance is performed by personnel having specified skill levels, using prescribed procedures and resources, at each prescribed level of maintenance and repair. MTTR is the sum of corrective maintenance times at any specified level of repair, divided by the total number of failures within an item repaired at that level, during a particular interval under stated conditions.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRM0010 | The Tenderer shall provide in its response the MTTR estimates and prediction for each of the following: - Line Replaceable Unit (LRU); - Each major equipment; |  |
| VCRM0020 | The Tenderer shall state in its response the average turn-around time (TAT) for a Line Replaceable Unit (LRU). |  |
| VCRM0030 | Malfunctions shall be indicated visually at the Technical Monitoring and Control System. |  |
| VCRM0040 | Automatic fault monitoring of all power supplies, and optional external alarms shall be provided. |  |
| VCRM0050 | If a faulty component will be changed the Technical Monitoring and Control System shall provide the opportunity to acknowledge after system setup. No manual adjustments shall be necessary. |  |
| VCRM0060 | An error log file shall be available for a continuous error report. |  |

### Availability

For the purpose of this specification, Availability is defined as a ratio of the total time the system is capable of performing its mission, against the time for which it is required to perform that mission, expressed as a percentage. The availability calculation excludes all planned downtimes.

The figures for Availability quoted in this Specification are for Operational Availability (Ao) and shall be calculated using the following equation:

Ao =

MTBF = Mean Time Between Failures in hours.

MTTR = Mean Time To Repair in hours.

MRT = Mean Response Time in hours (i.e. the average time from a notification of failure for a technician to be ready to commence a repair action).

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRA0010 | The VCS shall provide an inherent availability of at least six 9’s (>99.9999%). |  |

Note: Inherent Availability is defined as the probability that a system or equipment, when used under specified conditions, not considering delays due to the support environment (i.e. readily available tools, spares, maintenance personnel, etc.), will operate satisfactorily at any point in time, as required.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCRA0020 | The lifetime of the VCS shall be not less than 15 years or 130.000 hours operation. |  |
| VCRA0030 | All calculation shall be provided to indicate the system ability to meet the requirements with full explanation of all assumptions. |  |
| VCRA0040 | Upon outage of a single redundant server no radio calls shall be lost. |  |
| VCRA0050 | Failover of a single redundant server components shall be without audio loss for radio calls. |  |
| VCRA0060 | Air/Ground Audio switchover upon failure of a network segment or server shall be in less than 600 ms (non-perceivable outage). |  |
| VCRA0070 | A single failure shall not cause loss of more than one working position or one interface card. |  |

## Network Requirements

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VCNR0010 | The main components of the VCS shall be connected to a redundant network core via dual Ethernet links. |  |
| VCNR0020 | In case a redundant Ethernet link fails, the network connectivity shall be ensured by the remaining functioning network link, and VCS operation shall be unaffected (no calls are dropped). |  |
| VCNR0030 | The VCS shall automatically recognize the presence of the recovered links, without the need of the manual intervention. |  |
| VCNR0040 | The VCS shall support geographical redundancy. A subset of VCS components shall be possible to be split and installed at different geographical locations linked by the same VCS layer-3 network. |  |

## Interoperability

The role of the Tenderer, is to ensure and declare compliance of its EATMN constituent with the essential requirements, specific requirements contained within the relevant implementing rules for interoperability and other relevant technical specifications (e.g. Community specifications, standards).

The purpose of the following requirements is to ensure that the procured and implemented system is compliant by all means with the requirements laid down in the REGULATION (EC) No 1070/2009 on the interoperability of the European Air Traffic Management network.

Instruction to tenderers:

Tenderer shall assure compliance with the regulatory requirements, directives and applicable standards.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| FTIO0010 | The Tenderer shall attach with the tender documentation the EC Declaration of Compliance for all parts of the equipment/system (the Constituents) that is part of the offer and future delivery. |  |
| FTIO0020 | The Tenderer shall prepare and attach with the system documentation the EC Declaration of Suitability for use for the delivered VCS. |  |

# VCS – System Integration Platform

## General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SIGE0010 | The VCS integration platform shall be a host following applications with possibility to expand: - The Voice Communication System, by addition of supplementary equipment (e.g. OWPs, etc.); - Supports integration of 3rd party systems for future expansion needs (e.g. SATPHONE, ATM Systems). |  |
| SIGE0020 | The purpose of the integration platform shall be: - Ability to connect multiple applications including 3rd party and share data among them; - Capable to interoperate with existing umbrella management system via SNMP; - Centralised and integrated technical monitoring and control for multiple equipment. |  |
| SIGE0040 | The VCS integration platform shall be flexible and allow functional expansion by software. |  |
| SIGE0070 | The platform shall allow site separation and each site shall be able to automatically take over the other site as part of a disaster recovery concept (e.g. two different equipment rooms). |  |
| SIGE0080 | The VCS integration platform shall provide an element management system for the installed equipment. |  |

## Multiple Site Operation

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SICM0010 | The system shall allow multiple site operation with one backend system. This means that remote working positions for a fully integrated application shall be possible. |  |

## Monitoring

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SIMO0010 | The integration platform’s overall monitoring system shall monitor the status of the system elements that are installed. |  |
| SIMO0020 | The monitoring system shall display the health state of all components (e.g.: OK or problem). |  |
| SIMO0030 | The monitoring system shall monitor CPU load, disk and memory usage and present this information. |  |
| SIMO0040 | The monitoring system shall allow to modify the rules and threshold which trigger a warning or error. |  |
| SIMO0050 | An upward SNMP based interface to an umbrella management system shall be provided to obtain the overall system status. |  |
| SIMO0060 | All the elements needed for configuration, monitoring and logging shall have a web-browser based access. Credentials are required to access the elements. |  |
| SIMO0070 | The Monitoring tool of the TMCS shall perform: - Reporting of system events (e.g. change of system status, occurrence of failures); - Fault diagnosis; - The system shall provide infrastructure maps for consistent overview of the deployed system; - Statistics about system elements’ availability shall be produced. |  |

## Security & Safety

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SISS0010 | The Tenderer/Contractor shall provide the operational security guidelines that are applicable for his products. |  |
| SISS0020 | To minimize the network attack surface, all network reachable services deploy a “deny all” rule by default. Only ports which are explicitly documented and defined in the service descriptor configuration are allowed. The service descriptor configuration is only accessible by a privileged account holder. |  |
| SISS0040 | The VCS system shall be developed in full compliance with EUROCAE ED-153 software assurance level 3 (SWAL3). |  |

## IT Security

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SIIS0010 | Due to IT Security demands it is assumed that the system will not stay the same once it is in operation and therefore the system shall support an active software lifecycle. |  |
| SIIS0030 | The testbed shall be used as an automated regression test platform to ensure newly added functions do not impair existing functions. |  |

## System Design

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SIPD0010 | The system shall provide a reliability concept without a single point of failure (besides interfaces and working position). |  |
| SIPD0020 | The system shall be based on a layered architecture to guarantee that a change in a lower layer (e.g. communication protocol to a sensor) does not affect all other layers. |  |
| SIPD0030 | All components (except OWP and line interface cards) shall be redundant. |  |
| SIPD0040 | All network connections shall be redundant. |  |

## Test and Deployment system – Testbed

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SITD0010 | A testbed shall be available in order to conduct the verification and installation of application software and adaptation updates. |  |
| SITD0020 | The testbed shall include all components of the operational system, with 1 interface for every type of line used in the system, and 2 operator working positions for testing purposes. |  |

# Logistic Support

## Maintenance Concept

Maintenance of this system and associated environmental features will be efficient and responsive to operational needs and the requirements of aviation safety.

There are two levels of maintenance:

- "Level one": on-site, where the staff will isolate and replace faulty LRUs and SRUs, and

- "Level two": performed either in the Repair Workshop (at the Contractor's premises) or on-site (technical staff of Slovenia Control), or exceptionally, at any other site agreed between the Contractor and the Contracting authority. Faulty LRUs and SRUs will be repaired down to the component level, to a maximum possible extent.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSMC0010 | The Tenderer shall propose his own vision and concept of the most appropriate and the most efficient maintenance approach (especially corrective maintenance). |  |
| LSMC0020 | The Contractor shall guarantee the shortest possible MTTR (Mean Time to Repair), which shall be less than 2 hours. |  |
| LSMC0030 | The Contractor shall support the establishment of a support and, if necessary, service agreement with local companies covering the repair/replacement of COTS items by the original suppliers. |  |
| LSMC0040 | The Contractor shall guarantee support and repair/replacement of all hardware, software and documentation (including COTS products as well), including the supply of spare parts for a period corresponding to the expected life of the system, but not less than 15 years. |  |

## Spares and Support

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSSU0010 | The offered initial set of spare parts shall be specified in a tender documentation, in a form of the Mandatory Spare Parts List, which shall contain all spare parts (LRUs, SRUs, consumables), with the price for each individual item. |  |
| LSSU0020 | A Spare Parts List shall, for each spare part, include: - Contractor/Manufacturer Name, - Part Number (P/N), - Spare Part Description, - Recommended Quantity of Spare Parts to be delivered, - Quantity of parts to be installed in the system, - MTBF, MTTR, TAT, DT of each part, - Category: repairable (repair/replace on site, repair in repair workshop) or non-repairable (discard on failure), - Warranty period (only in case of specifically defined warranty period for certain parts). |  |
| LSSU0030 | If at the end of the warranty period it is proven that the measured spares consumption and/or MTBF is not within the limits as defined in the Contract, the Contractor shall review its spares calculations, as well as upgrade and supply the spares package at its own cost. |  |
| LSSU0040 | The Contractor shall guarantee the shortest possible TAT (turn-around time) for parts sent to the Repair Workshop for repair or exchange, which shall be less than 30 calendar days. |  |
| LSSU0050 | The Contractor shall guarantee the shortest possible DT (delivery time) for parts that will be additionally ordered by the Contracting authority, which shall be less than 60 calendar days. |  |
| LSSU0060 | The Contractor shall deliver all spare parts to the Contracting authority, in the quantity and quality which is in accordance with the Contract requirements, at the latest 7 calendar days before the start of commissioning. These spare parts shall be inspected and tested (except consumables) during the Site Acceptance Test (Guarantee Test). |  |
| LSSU0070 | The Contractor shall notify the Contracting authority if the delivery of a particular type of spares is becoming difficult or if the manufacturing of that part has stopped. Such notification accompanied by a spare parts replacement proposal shall be given at least 6 months in advance. |  |
| LSSU0080 | The above stated requirement (LSSU 0070) shall be valid for parts procured from the Contractor or any of the suppliers involved in the procurement of spare parts for this system. |  |
| LSSU0090 | The Contractor shall include technical customer support maintenance by a professional/specialist ATC VCS engineer, based in the Contractor’s premises. Upon contract signature, the Contractor shall provide the contact details (Name/Surname, Title, Position/Department, Telephone, Fax, E-mail address, Office Working time) for the entitled professional mentioned above. |  |

### Mandatory Spare Parts List

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSSL0010 | The Tenderer shall include in its offer a mandatory set of spare parts to enable the efficient seven (7) years maintenance of all parts of the system, and for each site separately. The Contracting authority reserves the right to procure an additional set of spares. |  |
| LSSL0020 | The offered initial set of mandatory spare parts shall be based on the RAM calculation, but not less than one complete set of spares with minimum: - Qty. 1 of each item for system quantities <=3; - Qty. 2 of each item for system quantitiy between 4 and 10; - Qty. 4 of each item for system > 10. |  |
| LSSL0030 | The Tenderer shall include in its offer also a mandatory set of spare parts for the TMCS. |  |
| LSSL0040 | The offered mandatory set of spares shall be of the same type/model/version as the equipment installed. |  |

### Recommended spare parts

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSSL0050 | The Tenderer is encouraged to propose an additional set of spare parts according to its own experience and maintenance concept, which shall be useful. This list shall be clearly divided from a Mandatory Spares Part list from 6.2.2. |  |

## Warranty

### General

Warranty is the firm and written obligation of the Contractor to fix, at its costs and over an agreed period, the defects and deficiencies occurring on the accepted deliverables (hardware, software, documentation, etc.).

This obligation does not apply when the Contractor can prove that such defect or deficiencies fall outside the warranty coverage.

### Warranty Period

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSWP0010 | The warranty period for all HW and SW mentioned above shall be at least 48 months from the date the Site Acceptance is approved - signing the Site Acceptance Certificate by Contracting Authority and Contractor submits to the Contracting Authority Bank Guarantee for elimination of defaults within warranty period. |  |
| LSWP0020 | The Contractor’s obligation to correct defects and deficiencies shall apply until all the reported and pending defects and deficiencies from the Site Acceptance, as well as from the warranty reporting period, have been corrected in a satisfactory way. |  |
| LSWP0030 | The warranty reporting period for the HW/SW items and documentation shall automatically be extended by the period during which the VCS (per site) is not operationally available (DOWN TIME). |  |
| LSWP0040 | After the warranty reporting period, any newly detected deficiencies shall not fall under the warranty any longer. |  |

### Obligations of the Contractor

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSWO0010 | If defects and deficiencies affecting the contractually agreed supplies and services arise during the appropriate warranty period, the Contractor shall begin to rectify such defects in compliance with the provisions listed hereinafter. |  |
| LSWO0020 | Where the warranty period is concerned, it is generally agreed that, in case of the Contractor receiving a notification in the time from Monday to Friday, 8:00 to 16:00 hours, rectification of the defects shall begin within 5 working days after the receipt of the Contractor’s notification. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSWO0030 | In this respect the Contractor shall guarantee a support service for the above mentioned periods. Based on a detailed description of the fault, an appropriate system specialist shall, without delay, contact by telephone the Slovenia Control’s personnel who have given the notification of the fault. |  |
| LSWO0040 | Where complex system faults are identified, the project managers shall reach an agreement regarding the suitable location for troubleshooting and regarding deadlines. |  |
| LSWO0042 | Where complex system faults are identified, the contractor should ensure that support team specialists will be present on-site in less than 3 (three) hours from the notification. |  |
| LSWO0050 | Upon expiry of the above deadlines Slovenia Control may rectify the fault by itself, or have it rectified at the Contractor’s expense. The Contractor’s warranty obligation shall thereby remain unaffected if the work has been performed properly and Slovenia Control has informed the Contractor thereof without delay. |  |
| LSWO0060 | The rectification of faults and any other work performed on accepted or operational systems shall be carried out in compliance with the Slovenia Control’s internal work instructions; where applicable, special arrangements will be made in individual cases. |  |
| LSWO0070 | After completion of the repair or modification the Contractor shall demonstrate the compliance with the specification of the HW/SW and Documentation. |  |
| LSWO0080 | A report (including a Version Description Document for SW items) describing the nature of the deficiency/defect, the cause and the corrective measures taken, shall be prepared by the Contractor and submitted to Slovenia Control with the correction. |  |
| LSWO0090 | Replacement parts already delivered to Slovenia Control may be used by the Contractor during the warranty period. |  |
| LSWO0100 | The Contractor shall provide replacements, at no expense to Slovenia Control, for defective parts during the warranty period. |  |
| LSWO0110 | The Contractor shall correct, at no expense to Slovenia Control, all defects in the design of hardware or software during the warranty period, where these defects cause the system not to meet specified performance requirements. |  |
| LSWO0120 | Fixes to the software shall undergo regression testing. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| LSWO0130 | The documentation shall be updated as required to reflect the HW/SW deficiencies corrected under the warranty. |  |
| LSWO0140 | During the warranty period, the Contractor shall provide support to Slovenia Control in solving any problem arising from the license arrangements that the Contractor has negotiated with the vendors in place and name of Slovenia Control. |  |

# Technical System Documentation

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| TSDO0010 | The documentation shall be compliant by all means with the requirements laid down in the Regulation (EC) No 1070/2009. |  |
| TSDO0020 | The documentation shall be provided in English. The information contained shall be complete, accurate, and as simple and brief as possible. Consistent terms shall be used throughout the documentation sets. A glossary is recommended. |  |
| TSDO0030 | Each manual shall be uniquely identified. It shall additionally contain documentation version, change history, publishing date, product version (if applicable) and issuing organisation. |  |
| TSDO0040 | In a dedicated section, each manual shall describe the target group and its needs, as well as purpose, structure and use of the document, and warnings and/or cautions. |  |
| TSDO0050 | For navigation purposes, each manual shall at least contain a table of contents, and an index (if applicable). Additional navigation elements are recommended. Electronic media shall equally provide navigation support to allow fast access to information. Users shall always be able to determine their location within the electronic document, and all locations to which they can move from their current location. |  |
| TSDO0060 | Instructional parts of the documentation shall provide procedural information according to the user’s tasks. Reference documentation shall allow random access to individual units of information. |  |
| TSDO0070 | The system documentation for each site shall consist of: - Hardware documentation, - Software documentation, - Operational user manual, - Training documentation, - Site installation documentation. |  |
| TSDO0080 | The final versions of the system documentation shall consist of 1 hard copy per site and 1 copy on CD or USB stick. |  |
| TSDO0090 | The system documentation shall be written and printed in accordance with either ISO A4 or ISO A3 format standards. All drawings shall be documented in a commonly available CAD/MSVisio utility. |  |
| TSDO0100 | The Tenderer shall specify a list of all system documentation specifying reference numbers (if applicable at the time of tender procurement), description of documentation, delivery milestones in relation to project milestones (Contract Signature, FAT, SAT, etc.) |  |
| TSDO0110 | The Tenderer shall also supply for each site the COTS documentation i.e. a set of technical documents of the system hardware and software units, provided by the manufacturer of COTS products (such as PCs, clients, modems, network equipment). These documents shall be delivered in the same quantity as the system documentation. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| TSDO0120 | Defects, misunderstandings, inadequate or incomplete descriptions and other findings in the documentation, which compromise the quality of the documentation and/or influence the usability of the documentation for the planned purposes, shall be corrected without any extra costs to the Contracting authority. |  |
| TSDO0130 | All documentation to be delivered shall be issued in a final version and provided to the Contracting authority, prior to the Site Acceptance. |  |
| TSDO0140 | The documentation shall include the following: - Equipment description; - Equipment block diagram; - Unit layout in racks and rack wiring; - Detailed description and purpose of each unit; - Interconnections within units; - Wiring and assembly diagrams down to the LRU/SRU level; - Fault finding diagrams; - Setting-up and operating procedures; - Preventive maintenance and its procedures; - Corrective maintenance and its procedures; - Specification of all equipment units with part number, serial number and manufacturer; - Other information necessary to perform regular and preventive maintenance. |  |
| TSDO0150 | The software documentation (e.g. the Software User Manual or equivalent and the Version Description Document or equivalent) shall contain a description of the system software and shall comprise sufficient details to permit full understanding and maintenance of the system. |  |
| TSDO0160 | The documentation shall provide guidelines for the technical staff to: - Understand the equipment function in detail; - Perform preventive and corrective maintenance of the equipment; - Troubleshoot the system down to the LRU/SRU level; - Install and configure any LRU/SRU in case of complete equipment failure or malfunction of that LRU/SRU; - Perform all necessary measurements and adjustments. |  |

# Training

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| TRNG0010 | The training for the equipment shall be fully compliant with the ATSEP.OR.215 System and equipment rating training requirement of Commission Implementing Regulation (EU) 2017/373 of 1 March 2017 laying down common requirements for providers of air traffic management/air navigation services and other air traffic management network functions and their oversight, repealing Regulation (EC) No 482/2008, Implementing Regulations (EU) No 1034/2011, (EU) No 1035/2011 and (EU) 2016/1377 and amending Regulation (EU) No 677/2011 (OJ L 62, 8.3.2017, p. 1–126). |  |
| TRNG0020 | The following training of personnel is required: - System and equipment rating training of existing COM qualified ATSEP. |  |
| TRNG0025 | The Tenderer shall define the course manager and compliance monitioring manager for the TRNG0020 training and their competencies after contract signature. |  |
| TRNG0030 | The Tenderer shall submit in its offer an initial version of the Training Plan. The Training Plan shall be discussed in detail with the Contractor and approved by the Contracting authority in accordance with the agreed schedule. |  |
| TRNG0040 | The Tenderer shall suggest a maximum number of trainees. The number of trainees shall not be less than six (6). |  |
| TRNG0050 | In compliance to the ATSEP.OR.215 as per TRNG0010, the technical staff shall be trained by theoretical, practical and on-the-job training as well as to: - Understand equipment architecture and configuration, - Understand operational functions and features of all equipment units, - Understand and use system software application(s) which are part of delivered equipment, - Perform preventive maintenance of the equipment, - Perform corrective maintenance, i.e. troubleshoot the system down to the LRU and SRU or component (where applicable) levels, - Perform system test and alignment procedures for LRU/SRUs, - Perform required measurements and adjustments and to be able to use all necessary tools and instruments, - Understand the diagnostic and test utilities and procedures. |  |
| TRNG0060 | The Training shall address all of the hardware and software delivered in the scope of the Contract, which means that the training for installation, maintenance and operation of COTS products shall be included in the Tender Documentation and in the Training Plan, as well. |  |
| TRNG0070 | The training language shall be English or Slovenian. The Contractor shall provide necessary training on all products delivered within the project. |  |
| TRNG0080 | Contractor shall ensure that personnel engaged in the theoretical and practical on-the-job training of Contracting authority ATSEP shall be fluent in English or Slovenian, and are suitably qualified to perform task of training instructor as well as competence assessor and experienced in the system domains ad per TRNG0050. |  |
| TRNG0090 | The content of the theoretical (theoretical training syllabus and theoretical training objectives) and practical (practical training syllabus, including practical exercises and the tools and instruments used for the practical hands-on training and pactical training objectives) training courses, and on-the-job training during installation (on-the-job training objectives), shall be included in the Training Plan and shall be approved by the Contracting authority. |  |
| TRNG0100 | The training material in electronic form (on CD or USB stick) shall be made available for the trainees at least 1 week before the course begins. Paper copies of the training material shall be available for the trainees at the time the course begins. |  |
| TRNG0110 | The Contracting authority shall have the right to use such material for further courses within its own organisation. |  |
| TRNG0120 | The system and equipment rating training of ATSEPs shall be applicable to the duties to be performed and include the following: (1) theoretical courses; (2) practical courses; (3) on-the-job training during system installation. |  |
| TRNG0130 | A detailed ATSEP training schedule for the training elments of TRNG0120 shall be defined after contract signature and approved by the Contracting authoirity. |  |
| TRNG0140 | The Tenderer shall conduct a final written examination and practical assessment for each trainee (student) at the end of the training. A Trainee shall be considered as competent ("A trainee successfully completed the course.") for system maintenance and operation if he passes a practical assessment with a score of at least 75% and a theoretical (written) examination of at least 75%. |  |
| TRNG0145 | Contracor shall define the procedure in the event that an individual candidate fails to achieve the training objectives or fails to complete the training within the stipulated time of the training. |  |
| TRNG0150 | After the completion of each course, the following reports shall be provided to the Contracting authority: - Final training log book for all training elements of TRNG0120 signed by the Contractors head of training; - Each student's performance during each training element of TRNG0120; - A summary report for practical assessment of each student; - A copy of theoretical examination for each student; - An attendance report; - Certificate of competence for each student who successfully completed a course with a score of at least 75% for each exam. The certificate of competence shall have the information about name and surname of the candidate, date of the successfully competed course and the information, that the candidate passed the associated examination. The certificate of competence shall be issued on the Conractor’s letterhead. |  |
| TRNG0160 | The technical staff shall be trained in the first phase (see chapter 1.2 “Scope”) several parts: - Prior to FAT (Factory Acceptance Test) to be able to take part in Factory Acceptance Tests, held in the Contractor’s training facilities (Factory Training – theoretical and practical); - During the system installation, which will be considered as an on-the-job-training, as it is intended that trainees participate in installation activities as much as possible, while the Contractor shall make the supervision and have the responsibility of correct system installation. The Contractor is required to perform at least 12 hours of pre-installation training as part of theoretical training in order that the Contracting authority’s technical staff will be able to actively participate in the system installation. |  |
| TRNG0170 | The duration of the required ATSEP theoretical training course and practical training course shall last at least 10 working days with 75 training hours at least, including pre-instalation part of theoretical training as per TRNG0160. |  |
| TRNG0180 | The theoretical VCS training course programme shall at least consist of: - Theory of operation, system architecture, block-schemes, HW modules, front and back panels, - Racks equipment, cabling installation, wiring and cabling, equipment fitting and connecting, AC/DC power distribution and cabling, grounding and fusing, EMP protection, - System functions, SW, applications, menus, configuration, parameters, roles, missions, - Connections, integration, installation, - System maintenance, monitoring, site/equipment management, user/password management, troubleshooting. |  |
| TRNG0190 | The practical VCS training course programme shall at least consist of: - The maintenance terminal, - Practical “hands-on” training is required, practical fault finding, practical tips etc., - Usage of tools and instruments. |  |
| TRNG0200 | Contracting authority covers travel and accommodation costs, incurred with attendance of Contracting authority’s technical staff to training. All other costs, related to training, are included in contractual price. Contracting authority unilaterally designates trainees. |  |
| TRNG0210 | The Contractor shall issue Certificates of competence for the ATSEP personnel who successfully completed the System and Equipment Rating Training in accordance with the ATSEP.OR.215. |  |
| TRNG0220 | The Contractor shall monitor compliance of training to the requirements from TRNG0010 to TRNG0210. |  |
| TRNG0230 | The Contractor shall grant the Contracting authority access to the premises and applicable documentation for the purposes of TRNG requirements compliance monitoring by the Contracting authority, including access to the documentation of TRNG0220 compliance monitoring conducted by the Contractor itself. |  |

# Safety, Quality and Security Assurance

## Safety

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SARQ0010 | When creating the safety documentation, including a safety plan and safety reports, the Contractor shall take into account these ATM and programme related applicable standards/regulations/directives (and any amendments of documents released before the establishment of the contractual relationship in which this document is referenced): - Regulation (EC) No 552/2004 of the European Parliament and of the Council of 10 March 2004 on the interoperability of the European Air Traffic Management network (the interoperability Regulation) (OJ L 96, 31.3.2004, p. 26–42); Latest consolidated version: 11/09/2018; - Regulation (EC) No 1070/2009 of the European Parliament and of the Council of 21 October 2009 amending Regulations (EC) No 549/2004, (EC) No 550/2004, (EC) No 551/2004 and (EC) No 552/2004 in order to improve the performance and sustainability of the European aviation system (OJ L 300, 14.11.2009, p. 34–50); - All Directives, Community Specifications and Implementing Rules related to 3. and 4.; - EUROCONTROL Guidelines on conformity assessment for the Interoperability Regulation of the Single European Sky (IOP, EUROCONTROL-GUID-137), 2012-02-20, Edition 3.0; additionally, the Contractor shall provide the verification specifications and the verification records upon request; - IEC 61078 (RMA) Analysis techniques for dependability - Reliability block diagram and Boolean methods; - AIR NAVIGATION SYSTEM SAFETY ASSESSMENT METHODOLOGY (SAM) of EUROCONTROL, 2.2 - Regulation (EU) No 376/2014 of the European Parliament and of the Council of 3 April 2014 on the reporting, analysis and follow-up of occurrences in civil aviation, amending Regulation (EU) No 996/2010 of the European Parliament and of the Council and repealing Directive 2003/42/EC of the European Parliament and of the Council and Commission Regulations (EC) No 1321/2007 and (EC) No 1330/2007 (OJ L 122, 24.4.2014, p. 18–43); Consolidated version: 11/09/2018; - Commission Implementing Regulation (EU) 2017/373 of 1 March 2017 laying down common requirements for providers of air traffic management/air navigation services and other air traffic management network functions and their oversight, repealing Regulation (EC) No 482/2008, Implementing Regulations (EU) No 1034/2011, (EU) No 1035/2011 and (EU) 2016/1377 and amending Regulation (EU) No 677/2011 (OJ L 62, 8.3.2017, p. 1–126); Consolidated version: 05/11/2020. |  |
| SARQ0020 | Safety reports shall include the safety recommendations to Slovenia Control, as a possible means for risk mitigation. This shall include procedural and human mitigations, e.g. training, shift management, maintenance procedures, operational procedures etc. |  |
| SARQ0030 | The safety documentation shall be provided to the Contracting authority for review and approval in accordance with the milestones specified in the Documentation Plan. |  |

### Safety Audit

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SASA0010 | The safety audit shall be conducted by the Contracting authority in duration of approximately one working day according to the Contracting authority’s safety audit plan previously delivered, subject to mutual agreement. |  |
| SASA0020 | The safety assurance process shall be audited and the Contractor shall provide full support to the Contracting authority’s safety audit team including access to evidence and arguments. |  |

### Safety Plan

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SASP0010 | The Contractor shall provide a Safety Plan which shall include all activities to be performed by the Contractor to meet the requirements related to safety, in such a way that the delivered technical system is safe for operation and minimises the risks which may contribute to aircraft accidents as far as reasonably practicable. |  |
| SASP0020 | A preliminary version of the Safety Plan shall be delivered at the latest 30 days after contract signature, and shall be reviewed and approved by the Contracting authority. |  |
| SASP0030 | Safety activities to be specified in the Safety Plan shall be carried out to cover: - All hardware and software to be delivered (components to be developed, procured, modified, or re-used), up to external interfaces of the system, - Safety related procedures and training of the Slovenia Control’s staff, - The whole time span of the Project and all activities with safety significance, i.e. the system specification, design, development, integration, installation, acceptance, commissioning, transition to operation and maintenance of the system. |  |
| SASP0040 | The Contractor shall produce updates of the Safety Plan, if necessary. |  |

### Safety Reports

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SASR0010 | Safety reports shall cover the Safety Assessment process, containing as a minimum, the following: - Hazards identification and analysis for each system function, including the determination of hazard likelihood and severity, and possible effect on operation, - Identification of possible effect on operation for each hazard, - Identification of risk mitigation measures for each hazard. |  |
| SASR0020 | Safety Reports shall be produced in accordance with the Safety Plan. |  |
| SASR0030 | Safety Reports shall include, as a minimum, the following set of documents and due dates: - Functional Hazard Assessment Report (FHAR), due date: 30 days after contract signature; - Preliminary System Safety Assessment Report (PSSAR), due date: 2 calendar weeks before the FAT starting date; - System Safety Assessment Report (SSAR), due date: 1 calendar week before installation of the target system; - Safety Issue Log (SIL). The document shall contain all safety critical issues which shall be mitigated in a procedural or human related matter. Due date: Start of the equipment installation; - Software Safety Folder. The Contractor shall use the Guidelines for ANS Software Safety Assurance, EUROCAE document ED-153. |  |

### Software Safety Requirements

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SASS0010 | These ATM and programme related applicable standards/regulations/directives (and any amendments of documents released before the establishment of the contractual relationship in which this document is referenced) are applicable for software safety assurance: - Annex IV to ED Decision 201/022/R of 30 Oct 2019 establishing a software safety assurance system to be implemented by air navigation service providers; - As a means of compliance with Annex IV to ED Decision 201/022/R ED-153/EUROCAE GUIDELINES FOR ANS SOFTWARE SAFETY ASSURANCE. The Contractor shall produce evidence and arguments demonstrating that: - the software safety requirements correctly state what is required by the software, in order to meet safety objectives and requirements, as identified by the risk assessment and mitigation process; - traceability is addressed in respect of all software safety requirements; - the software implementation contains no functions which adversely affect safety, particularly there must not be the CSCI whose single failure would induce the effect with severity class 1 as per ESARR 4; - the software satisfies its requirements with a level of confidence which is consistent with the software criticality; - assurances are provided confirming that the general safety requirements set out in the previous points are satisfied, and the arguments that demonstrate the required assurances are at all times derived from: - a known executable version of the software; - a known range of configuration data; - a known set of software products and descriptions, including specifications that have been used in the production of that version. | h |
| SASS0020 | The Contractor shall allocate software assurance levels (SWAL) to all operational software, in compliance with the following: - The software assurance level shall relate the rigour of the software assurances to the software criticality by using the severity classification scheme of the Contracting authority combined with the likelihood of occurrence of a certain adverse effect. A minimum of four software assurance levels shall be identified, with software assurance level 1 indicating the most critical level (if such software exists); - An allocated software assurance level shall be commensurate with the most severe effect that software malfunctions or failures may cause. This shall, in particular, take into account the risks associated with software malfunctions or failures and the architectural and/or procedural defences identified. - Software components that cannot be shown to be independent of one another shall be allocated the software assurance level of the most critical of the dependent components. |  |
| SASS0030 | To assure software safety requirements validity, the Contractor shall describe the functional behaviour of software in nominal and downgraded modes, timing performances, capacity, accuracy, software resource usage on the target hardware, robustness to abnormal operating conditions and overload tolerance, as appropriate. Software safety requirements shall be complete and correct, and compliant with the system safety requirements. |  |
| SASS0040 | To assure the software safety requirements verification, the Contractor shall ensure that: - The software functional behaviour, timing performances, capacity, accuracy, software resource usage on the target hardware, robustness to abnormal operating conditions and overload tolerance, shall comply with the software requirements. - The software shall be adequately verified by analysis and/or testing and/or equivalent means. - The software verification shall be correct, complete and documented. |  |
| SASS0050 | To assure the software configuration management, the Contractor shall ensure that: - Configuration identification, traceability and status accounting facilitate that the software life cycle data is shown to be under configuration control throughout the software life cycle. - Problem reporting, tracking and corrective actions facilitate that safety related problems associated with the software are shown to have been mitigated. - Retrieval and release procedures facilitate that the software life cycle data is regenerated and delivered throughout the software life cycle. |  |
| SASS0060 | To assure the software safety requirements traceability, the Contractor shall ensure that: - Each software safety requirement is traced to the same level of design at which its satisfaction is demonstrated. - Each software safety requirement, at each level in the design at which its satisfaction is demonstrated, is traced to a system safety requirement. |  |
| SASS0070 | The assurances from SASS0030 to SASS0060 shall include the rigour for each software assurance level which shall increase as the software increases in criticality. For that purpose: - the variation in rigour of the assurances per software assurance level must include the following criteria: - required to be achieved with independence; - required to be achieved; - not required; - the assurances corresponding to each software assurance level must give sufficient confidence that the software can be operated tolerably safely. |  |
| SASS0080 | For any software (such as COTS, non-developmental software or previously used software, etc.), for which some of the requirements cannot be applied, the Contractor shall provide, through other means, the same level of confidence as the relevant software assurance level whenever defined. Those means must give sufficient confidence that the software meets the safety objectives and requirements, as identified by the safety risk assessment and mitigation process. |  |

## Quality

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| QGEN0010 | The Manufacturer shall be certificated, holding a valid ISO 9001:2015 and ISO 14001 or equivalent Quality Management System Certificate. |  |
| QGEN0020 | The Tenderer shall submit documentary evidence in the Tender establishing to the Contracting authority satisfaction that the Manufacturer has a valid Quality Management System certificate. |  |

### Quality Assurance Plan

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| QAAP0010 | The Contractor shall develop a Quality Assurance Plan, subject to the approval by the Contracting authority. |  |
| QAAP0020 | The Quality Assurance Plan shall describe the organisation, processes, tasks and responsibilities with respect to quality assurance. |  |
| QAAP0030 | The Quality Assurance Plan shall identify the documents to be produced in appropriate phases of the lifecycle (see also the Project Management Plan), and shall state how these documents are checked for adequacy. |  |
| QAAP0040 | The Quality Assurance Plan shall identify the standards, practices, conventions and metrics to be applied and shall state how compliance with these items is to be monitored and assured. |  |
| QAAP0050 | The project applicable and referenced documents and standards shall be listed in the Quality Assurance Plan, with their title and version number. |  |
| QAAP0060 | The Preliminary Quality Assurance Plan shall be provided by the Contractor to the Contracting Authority within 10 working days from the day of the signature of the contract on. |  |
| QAAP0070 | The final version of the Quality Assurance Plan shall be available within 60 days from contract signature. |  |

### Quality Audit

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| QAQA0010 | The Quality Assurance processes, technical documentation and products produced shall be subject to quality audit. The date, schedule and scope shall be mutually agreed. |  |
| QAQA0020 | The duration of quality audit shall be approximately one working day. |  |
| ID | Requirements | Compliance YES/NO – references to evidence |
| QAQA0030 | The Contractor shall provide full support to the Contracting authority’s quality audit team including access to evidence and arguments. |  |

## Security

### General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SECG0010 | During the execution of the contract, the Contractor shall be able to provide evidence that a required security by design framework that includes documented secure software development, quality management system and ISMS has been adopted. |  |
| SECG0020 | The Contractor agrees with the performance of penetration tests as mentioned bellow and performed in accordance with the penetration testing best practices and / or standards by the customer. |  |
| SECG0030 | The Contractor shall provide competent interlocutors and / or engineers for performing penetration testing as well as person (contact information; name; rank, email, phone) responsible for maintaining security of the system. |  |
| SECG0040 | The Contractor shall include the penetration testing into project management timeline / deployment of the system as prearranged / agreed with the customer. The scope of each penetration test will be agreed in advance between Contractor and customer. |  |
| SECG0050 | The customer is planning on performing following penetration test; a) pre-production penetration testing – prior to deployment, b) production penetration testing – after successful installation on customer environment and c) penetration tests whenever a major changes are planned to be deployed on the system. |  |
| SECG0060 | In addition, external security audits can be performed during the execution of the contract: by the customer on the Contractor, or a 3rd party auditing party (customer outsources the auditing of the Contractor to a competent auditor). |  |
| SECG0070 | The Contractor shall inform the customer of any change that may materially impact the security of system (vulnerabilities, data leakage) within a period no longer than 48 hours. The Contractor will demonstrate to the customer that they have a process in place to enable this. |  |
| SECG0080 | The Contractor shall track, document and report to the customer as soon as possible, but no later than 48 hours from the security Incident being detected and propose remediation plan - solution no later than 72 hours and be able to implement the solution immediately after the conformation from the customer. |  |
| SECG0081 | The Contractor shall ensure that the system is designed with appropriate resilience to meet the agreed SLA. |  |
| SECG0090 | The Contractor must ensure that a capability is in place to log and monitor actions and events, and to detect unauthorised access and misuse of the system. |  |
| SECG0100 | The system shall log events, be capable of exporting logs in a secure manner to an external system and have audit functionalities to guarantee complete user and service processing accountability. |  |
| SECG0110 | The Contractor shall maintain and, if requested to do so by the customer, provide a list of staff (including subcontracted personnel) working on the system. |  |
| SECG0120 | Where appropriate, the Contractor’s staff (including any subcontracted personnel) shall be capable of obtaining/holding security clearances relevant to the areas they are required to access, as defined by the customer. |  |
| SECG0130 | The Contractor shall provide competent interlocutors and engineers for performing cyber security risk assessment of the contracting authority system. The duration / presence of competent Contractors personnel shall last at least 2 working days. |  |

### System Hardening (w.r.t. cyber security)

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SECH0010 | The system shall have adequate levels of protection against intrusion in order to, as far as is reasonably practicable, avoid unauthorised access, modification, or erasure of data by a third party. |  |
| SECH0020 | The system shall implement appropriate authentication mechanisms to validate the respective user credentials prior to providing access to the service (e.g. multifactor authentication) where appropriate. |  |
| SECH0030 | The system shall enforce the "Least Privilege Principle". |  |
| SECH0040 | The system shall enforce the "Separation of Privilege Principle"; Privileged User actions must be performed from dedicated Privileged User Accounts segregated from standard user accounts. |  |
| SECH0050 | The system shall have the capabilities to detect security incidents. |  |

### Security Training

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SECT0010 | The Contractor shall ensure that all Contractor’s personnel with access to the system or contracting authority data, receive information security training appropriate to their role, and responsibilities, including being made aware of relevant cyber security risks. |  |
| SECT0020 | The Contractor shall provide thorough system information to internal Security Operations Center (SOC), and perform training and familiarisation (relevant architecture disclosure, relevant network and dataflows disclosure, integration specifics where external, specific protocol definitions) for Slovenia Control SOC Personnel. The process shall last no longer than 2 days at the Controctor’s premises. |  |

### Security Recomendations

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| SECR0010 | The system shall be compliant with the Security Recommendations for VCS systems as defined in EUROCONTROL document DOC 10 – Voice over IP Security Baseline – Edition 1.0 (2020). |  |

# Project Management

## General

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMGE0010 | The Contractor shall be responsible for the management, performance, monitoring and coordination of the whole project from the project kick-off until the completion of the contract. |  |
| PMGE0020 | The Contractor shall establish a project organization in accordance with the requirements included herein, having necessary resources, qualification and experience to fulfill all of its obligations. |  |
| PMGE0030 | The Tenderer shall define and describe the part of its organization which will manage or be involved in the project. |  |
| PMGE0040 | The Contractor shall appoint the Contractor’s Representative, who will be an interface to the Contracting authority's Project Manager, and be at the Contracting authority’s disposal for all matters relating to contract execution. |  |
| PMGE0050 | In case another person will act as his substitute, the Contracting authority shall be notified at least 2 weeks in advance of the other person proposed to substitute him. |  |
| PMGE0060 | The Contractor's Representative (or his substitute) shall be present at all meetings during the contract execution. |  |
| PMGE0070 | The Contractor's Representative shall be responsible for project co-ordination and will take all necessary actions to ensure the project progress according to the agreed schedule. |  |
| PMGE0080 | Communication between the Contractor and the Contracting authority shall be in accordance with the Contracting authority's practice. Details of a Communication Procedure between the Contractor and the Contracting authority shall be defined by the Contracting authority. Concluded contract defines contact persons. |  |
| PMGE0090 | If deemed necessary during contract execution, the Contracting authority or the Contractor can propose progress meetings. |  |
| PMGE0100 | The agenda for this meeting(s) shall be mutually agreed and prepared at least 3 working days prior the date of a meeting. |  |
| PMGE0110 | The following persons shall be present at progress meetings: - The Contractor's Representative, - The Contracting authority's Project Manager, - Any other persons who the above representatives consider important to be present. |  |
| PMGE0120 | The venue of meetings shall be premises of Contracting authority or one of the locations (ATCC, Portorož, Maribor). Contractor covers all costs, related to attendance to the meeting (travel costs etc.). Meeting can be held on alternative location, if so agreed in writing by Contracting authority. |  |
| PMGE0130 | The Contractor shall prepare minutes of the meetings and submit them for approval to the Contracting authority not later than 3 working days after the meeting finishes. |  |
| PMGE0140 | The Contractor shall issue and manage a Progress Chart (Master Time Schedule). The contract shall be executed in accordance with the progress chart. This chart shall be set out in the form of a linear timetable (preferably using the MS Project). The starting date is to be the date of entering the contract into force. |  |
| PMGE0150 | The Progress Chart shall specify dates of all major actions and decisions to be taken by both the Contracting authority and the Contractor. Any alterations to this chart shall be examined and mutually agreed. |  |
| PMGE0160 | The initial progress chart shall be included in the tender documentation. |  |
| PMGE0170 | The progress chart shall be agreed between the Contractor and the Contracting authority and shall be kept updated during ontract execution. The version control of an electronic file of the Progress Chart shall be established. |  |
| PMGE0180 | The Contractor shall establish close coordination with the Contracting authority for the development of all planning activities related to the project, forwarding relevant plans, procedures, etc. for review and approval, prior to putting them into force. |  |
| PMGE0190 | The Contractor shall prepare at least the following Project Plans at the appropriate stage in the project for review and approval by the Contracting authority: - Project Management Plan (PMP), - Logistic Support Plan (LSP), - Documentation Plan (DP), - Safety Assurance Plan (SAP), - Quality Assurance Plan (QAP), - Training Plan (TP), - Installation and Commissioning Plan (IP), - FAT Plan and Procedures, - SAT Plan and Procedures. |  |

## Project Management Plan

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMPM0010 | The Contractor shall prepare a Project Management Plan (PMP) in accordance with the requirements included in the present chapter. |  |
| PMPM0020 | A draft version of the PMP shall be provided as part of the tender documentation. An initial official version of the PMP shall be provided by Contractor within 10 working days from the signature of the contract on. |  |
| PMPM0030 | The Project Management Plan shall include at least the following: - Project scope and overview, - Project deliverables (shall also include a Documentation List), - Work Breakdown Structure (Shall define the scope of work and resources necessary to meet the Contract requirements. The work breakdown shall also include the work to be performed by the Contracting authority, e.g. participation in reviews and tests, preparation of data.), - Project organisation and responsibilities, - Master Time Schedule (Progress Chart), - Quality assurance activities to be performed in the project by the Contractor, - Configuration management activities (regarding hardware, software and documentation version changes). |  |
| PMPM0040 | Any change to the PMP or to the processes outlined in it will be subject to the formal Contracting authority’s approval. The PMP shall be kept up-to-date. |  |
| PMPM0050 | The PMP shall normally include at least the following aspects: - Management procedures and practices; - Work breakdown structure (WBS); - Master time schedule, showing dates and deliverables; - Master resource plan, showing roles and responsibilities; - Key risks that might jeopardize the project. |  |

## Documentation Plan

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMDP0010 | A Documentation Plan shall specify the list of all documents to be delivered to the Contracting authority during contract execution. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMDP0020 | A draft version of the Documentation Plan shall be provided by the Tenderer in the tender documentation. An initial official version of the Documentation Plan shall be provided by the Contractor within 10 working days from the day of the signature of the contract on. |  |
| PMDP0030 | The Documentation Plan shall include at least the following: - Title of document, - The Contractor, - Applicability of the document (e.g. entire system, a certain subsystem or a particular COTS product, hardware documentation, software documentation, etc.), - Reference and version number of the document, - Dates of each document delivery. |  |

## Logistic Support Plan

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMLS0010 | The Contractor shall prepare a Logistic Support Plan (or equivalent) which shall specify in more detail logistic aspects of the Contract. The Logistic Support Plan shall include: - Maintenance concept of the system, - Maintenance activities, levels and responsibilities (maintenance flows overview), - Overview of the technical documentation to be provided, especially stating the manuals with maintenance procedures, - Spare Parts List which shall meet the requirements of this Technical Specification, - Relation of maintenance activities with the skills obtained at technical training, - Tools and test equipment list to be provided and/or required, - All aspects of warranty support including a detailed description of the scope of warranty support, - Possible post-warranty support arrangements regarding the system maintenance, - Overview of recommended preventive maintenance actions. |  |
| PMLS0020 | A draft version of the Logistic Support Plan shall be provided by the Contractor within 10 working days from the day of the signature of the contract on. |  |

## Installation and Commissioning Plan

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMIM0010 | On each site where installation is going to take place, the Contractor shall prepare an Installation and Commissioning Plan comprising: - The Contractor’s scope of work, - Sub-contractors involved and their scope of work (if applicable), - The Contracting authority’s scope of work, - Tasks to be performed and the person(s) responsible for each task, - Timing of the tasks, - Documentation (e.g. instructions, specifications, drawings, interconnection diagrams and other relevant information for installation), - Other information important for the final installation. |  |
| PMIM0020 | An initial (draft) version of the Installation and Commissioning Plan shall be provided in the tender documentation. |  |
| PMIM0030 | The final Installation and Commissioning Plan plan shall be submitted at least 4 weeks and approved by the Contracting authority at least 3 weeks before the start of installation activities. |  |

## Acceptance Test Plans and Procedures

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMAP0010 | The Contractor shall provide acceptance test plans and procedures (test specifications) for Factory Acceptance Test and Site Acceptance Test, including a detailed description of the proposed test techniques and procedures to verify all equipment parameters, together with a schedule for such tests. The following documents shall be provided: - Factory Acceptance Test Plan and Procedures, - Site Acceptance Test Plan and Procedures. |  |
| PMAP0020 | These acceptance test plans and procedures (test specifications) shall at least contain the following: - A schedule of the actions to be taken in the testing of various parts of the equipment, - The forms of documentation of test results, - The condition under which the tests shall be conducted and approved, - A detailed description of the tests to be performed. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| PMAP0030 | The FAT Plan and Procedures shall be submitted to the Contracting authority 4 weeks before the FAT at the latest. The document shall be reviewed by Contracting authority and shall be amended or changed if necessary, and approved by both parties 2 weeks before the FAT at the latest. |  |
| PMAP0040 | The Site Acceptance Test Plan and Procedures shall be submitted to the Contracting authority 4 weeks before the SAT at the latest. The document shall be reviewed by Contracting authority and shall be amended or changed if necessary, and approved by both parties 2 weeks before the SAT at the latest. |  |

# Installation and Commissioning/Transition

## Installation

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| INST0010 | The planning of the system installation and setting up shall be developed in close cooperation with the Contracting authority. |  |
| INST0020 | The Installation and Commissioning Plan, specifying all installation and transition activities, shall be approved by the Contracting authority prior to the installation. |  |
| INST0030 | The Contractor can perform a site survey before the installation takes place in order to identify necessary works to be performed, if deemed necessary. |  |
| INST0040 | The Contracting authority will perform, prior to the installation, a complete physical check of the goods received (equipment, accessories, spare parts, documentation, etc. – all according to the Contract specification), and will notify the Contractor if the delivery does not fulfill the requirements listed in the Contract Specification. |  |
| INST0050 | The Contractor shall have full responsibility for the system installation and setting up. |  |
| INST0060 | The Contractor shall produce, procure and supply all necessary equipment, tools, etc., consumable as well as non-consumable, needed for the installation and setting-up. |  |
| INST0070 | Installation on the site shall be conducted by Contractor’s skilled staff with support of the Contracting authority’s technical staff under close Contractor’s supervision. These activities shall form On-the-Job Training of the Contracting authority’s staff that shall be carried out during the installation in accordance with the agreed conditions given in the Training Plan. |  |
| INST0080 | The installation shall take into consideration all applicable local legislation rules and procedures. |  |
| INST0090 | The Contractor shall prepare a list of staff (for non-Slovenian residents) to conduct the installation activities, as well as all necessary documents early enough in order to obtain their working permits in the Republic of Slovenia (local legislation rules and procedures). |  |
| INST0100 | The Contractor shall state in the Installation and Commissioning Plan the aspects of the installation to be included in the documentation concerning: - Co-location aspects (where applicable); - Cabling arrangements, routing, identification; - EMC compatibility; - Earthing arrangements; - Equipment mounting, cooling, etc. |  |
| INST0110 | The Contractor shall specify all the facilities and procedures the Contracting authority has to provide for test purposes. |  |

### Racks

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| INST0120 | The VCS central equipment shall be based on a modular 19” rack concept. |  |
| INST0130 | The VCS equipment in the datacenter 1 shall be housed into 2 racks 42HE x 80 cm (width) x 100 cm (depth) with power distribution unit (PDU) with 16 A outlets. |  |
| INST0140 | The VCS equipment in the datacenter 2 shall be housed into 1 rack 42HE x 80 cm (width) x 100 cm (depth) with power distribution unit (PDU) with 16 A outlets. |  |
| INST0150 | Racks shall be provided by Slovenia Control. |  |
| INST0160 | VCS distribution frame shall be placed inside racks. |  |

### Environmental conditions

#### Environmental operational conditions

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| INST0170 | The system shall be able to work without degrading its performance under the following range of environmental conditions: - Ambient temperature range: 5º C to +40º C; - Humidity: 0 to 90% non-condensing. |  |

#### Environmental storage conditions

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| INST0180 | For storage purpose (not powered) the system shall support, without damaging consequences, the following range of conditions: - Temperature range: -25º C to +60º C; - Humidity: 0 to 95% non-condensing. |  |

### Power supply

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| INST0190 | The VCS shall normaly be fed from two main 230 V / 50 Hz AC independent Uninterruptible Power Supply (UPS) systems supplied by Slovenia Control (two separated UPS A and B sources). Slovenia Control will provide a power distribution units (PDU) with 16 A outlets and a proper earth connection. |  |
| INST0200 | All parts of the VCS including working positions shall be ready for doubled power supply (UPS A, UPS B). |  |
| INST0210 | The system shall operate without any degradation in the range 230 VAC +/-10%, 50 Hz +/-10%. |  |
| INST0220 | All performance requirements shall be achieved without readjustment when voltage vary between these specified limits. |  |
| INST0230 | Power supply for the operator working positions shall be suitable to fit into a double floor. The minimum length of the cable shall be 3m. |  |
| INST0240 | The failure of one power supply shall not be the cause for any system degradation. |  |
| INST0250 | In the case of single power supply failure the redundant power supply in operation shall have enough capacity to maintain operation. |  |
| INST0260 | Switching from one power supply to the other shall not cause any interruption of the service. |  |
| INST0270 | Supply and installation of power cables and adapters from AC outlets to the central and position equipment shall be included in the delivery (a length of 3m to be considered). |  |
| INST0280 | The offer shall include values for heat dissipation, power consumption and physical dimensions of all equipment that have to be delivered. |  |

## Pre-Commissioning and Completion

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| TCOM0010 | The Contractor shall issue a written notice to the Contracting authority when the installation within the site is finished and commissioning may commence. |  |
| TCOM0020 | The Contracting authority shall conduct an inspection of the site and the installation itself. |  |
| TCOM0030 | If some defects or deficiencies are found during the site inspection, the Contracting authority’s Project Manager shall notify the Contractor’s representative and list all of them in a Completion Report. The Contractor shall take necessary remedial actions at its own expense, and the procedure shall be repeated. |  |

## Commissioning and Transition

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| TTRA0010 | The Contractor shall be responsible for the commissioning and transition to the new system. Transition activities shall be performed in accordance with the final Installation Plan. |  |
| TTRA0020 | Transition to the new system shall be performed in a way that the functionality of the existing equipment is not significantly endangered at any moment in order to avoid/minimise the interruption of operational service. |  |

# Verification Requirements

Note: This section describes the plan for the testing of the VCS. The overall objective of the testing process is to verify that the delivered system meets the Contracting authority’s requirements, as defined in this specification.

## Test documentation

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VRTD0010 | The testing process shall be controlled and its progress monitored through the test documentation. |  |
| VRTD0020 | In the Test Procedure Book the conducted test cases shall be documented. |  |
| VRTD0030 | Test procedures and test reports shall be prepared for all the testing phases described below. |  |
| VRTD0040 | The test procedures shall be prepared not only to show conformance, but also to expose non-conformance with the requirements. |  |
| VRTD0050 | Deficiency reports shall be prepared whenever deficiencies are discovered. |  |

## System Test

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VRST0010 | The fully equipped system in the deliverable configuration shall be tested so as to verify that the system meets all specified requirements and is free from production errors prior to shipment. |  |

## Factory Acceptance Test

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VRFA0010 | Factory acceptance Test shall be performed with the fully equipped system in its deliverable configuration in order to verify that the equipment fully complies with the specification requirements. Non-complying equipment shall be rejected. |  |
| VRFA0020 | Factory acceptance shall be witnessed by the Contracting authority's representative(s). |  |
| VRFA0030 | All factory acceptance tests shall be normally carried out before the system installation and on the basis of a test specification submitted to Contracting authority by the Contractor at least 4 weeks before the FAT. |  |
| VRFA0040 | The Contractor shall provide a test specification (FAT Plan and Procedures) including a detailed description of the proposed test techniques and procedures to verify all equipment parameters, conditions under which the tests shall be conducted and approved, the forms of documenting test results, together with a schedule for such tests. |  |

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VRFA0050 | All equipment and sub-units shall be fully interconnected and built up into a complete system configuration. Specific tests considered as impracticable within the given system configuration will be performed using simulated inputs/outputs or a test bench when specifically approved by the Contracting authority. |  |
| VRFA0060 | All FAT procedures shall comply with and be performed according to the applicable standard documents, recommended practices or procedures. |  |
| VRFA0070 | The Contracting authority reserves the right to request some further tests to be performed (which are not listed in the FAT specification) if deemed necessary. These tests shall be also noted in the FAT report. |  |
| VRFA0080 | If a failure occurs during acceptance testing, the Contractor shall take necessary remedial actions at its own expense, and all relevant tests shall be repeated unless the Contracting authority decides otherwise. |  |
| VRFA0090 | After successful completion or unsuccessful attempt of the FAT, the FAT Report (including measurements) shall be immediately prepared and issued by the Contractor. The FAT report shall be signed by both the Contractor’s and Contracting authority’s FAT representatives. |  |
| VRFA0100 | After successful completion of the FAT, the FAT Certificate shall be issued by the Contractor. The FAT Certificate shall be prepared and signed by Slovenia Control’s Project Manager not later than 7 days after FAT completion and sent to the Contractor’s Representative according to the official communication procedure. |  |

## Site Acceptance Test

The purpose of a Site Acceptance Test (Guarantee Test) is to demonstrate Compliance of the delivered equipment and proper functioning of the system after commissioning, specified in the Contract.

| ID | Requirements | Compliance YES/NO – references to evidence |
| --- | --- | --- |
| VRSA0010 | The fully equipped VCS shall undergo site acceptance testing to ensure that the VCS will operate in accordance with the specifications outlined in this document when used in its operational environment. |  |
| VRSA0020 | The SAT shall be carried out after the system installation on each site on the basis of a test specification (SAT Plan and Procedures). |  |
| VRSA0030 | The Contracting authority reserves the right to request some further tests (site specific) to be performed (which are not listed in the SAT specification) if deemed necessary. These tests shall be also noted in the Site Acceptance Report. |  |
| VRSA0040 | The Site Acceptance testing (Guarantee Test) shall be performed by the Contractor’s and Contracting authority's representatives. |  |
| VRSA0050 | If a failure occurs during acceptance testing, the Contractor shall take necessary remedial actions at its own expense, and all relevant tests will be repeated unless the Contracting authority decides otherwise. |  |
| VRSA0060 | The Contractor is responsible for providing all test equipment (hardware and/or software) necessary for the tests. The test facilities provided by the Contractor are not part of the delivery. |  |
| VRSA0070 | All delivered spare parts shall be tested in real operation during the Site Acceptance Test. |  |
| VRSA0080 | The possibility of quick replacement of line replaceable units (LRUs) shall be demonstrated on the Site Acceptance Test (as a part of the On-the-Job training). |  |
| VRSA0090 | After successful completion or unsuccessful attempt of each Site Acceptance, a Site Acceptance Report (including measurements) shall be prepared and issued by the Contractor as soon as possible, but no longer than 7 days. The Site Acceptance Report shall be signed both by the Contractor’s and Contracting authority’s Site Acceptance representatives and approved by the Contracting authority’s Site Acceptance representative appointed. |  |
| VRSA0100 | Following satisfactory completion of all Site Acceptance Tests (Guarantee Test) the Contractor shall offer the System for formal acceptance by the Contracting authority. |  |
| VRSA0110 | Authorized Slovenia Control representatives shall grant the Site Acceptance if the following conditions are satisfied: - The inventory and a complete physical check of the goods received have shown that the delivery in all aspects fulfills the requirements listed in the Contract Specification; - The system has been installed correctly; - The documentation has been supplied and is in Compliance with the Contract Specification; - Training of the Slovenia Control’s staff has been carried out in accordance with the agreed conditions; - Spare parts have been delivered according to the Contract Specification and have been tested in real operation; - Site Acceptance tests have successfully been completed; - Signed and approved Site Acceptance Report has been issued. |  |
| VRSA0120 | All Site Acceptance Report problems and observations shall be closed or a relevant action assigned and agreed. |  |
| VRSA0130 | All Certificates of Conformance and Suitability for use shall be provided by the Contractor for all deliverable items (including software). |  |
| VRSA0140 | The Site Acceptance shall be granted by issuing a Site Acceptance Certificate by the Contractor. The Site Acceptance Certificate shall be prepared and signed by Slovenia Control’s Project Manager after completion of Site Acceptance. This might take up to 60 days from the day of signed SAT. |  |
| VRSA0150 | If any kind of certificate regarding the equipment will be requested by Civil Aviation Authority such document shall be provided by Contractor at no cost for Contracting Authority. |  |

……………………………….end of document ……………………………….