## RECAPITULATION
Fraport Slovenija, d.o.o.
JN-2023-B2-CIME/2/MF
DOBAVA KABLOV, KONEKTORJEV IN SVETILK ZA NOVO VOZNO STEZO TWY J IN OBNOVO ENEGA ODSEKA VOZNE STEZE TWY A
Delivery of cables, connectors and AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A
RECAPITULATION
LOT1: Delivery of cables, connectors for the new taxiway TWY J and renovation of one section of taxiway TWY A | SKLOP 1
PRIMARY CABLES | 0
PRIMARY CONNECTORS | 0
Summ | 0
LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A | SKLOP 2
TWY J LIGHT FIXTURES | 0
TWY A LIGHT FIXTURES | 0
TWY M LIGHT FIXTURES | 0
APRON BEFORE TWY M LIGHT FIXTURES | 0
LIGHT FIXTURES - spare parts | 0
Summ | 0

## General_remarks
Fraport Slovenija, d.o.o.
GENERAL REMARKS
Please see the article 3 from sample of contract (part of the documentation).
Public tender consists of 2 independent lots:
- LOT1: Delivery of cables, connectors for the new taxiway TWY J and renovation of one section of taxiway TWY A;
- LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A.
Light fixtures shall be used also in low visibility conditions (visibility less than 350 m, CAT III). Due to unification of inset light fixture types, all inset lights shall have wider light beam (allowed bigger displacement of cockpit from the centre line), light fixtures on curved sections shall have also mechanical toe in (15,75°) towards center of radius.
Offered lights shall be LED type.
Light fixtures shall comply following requirements:
- EASA CS-ADR-DSN, chapter M:
- general requirements for lights;
- taxiway centre line lights, visibility less than 350m
- inset stop bar lights, visibility less than 350m;
- elevated stop bar lights, visibility less than 350m;
- taxiway edge lights;
- runway guard lights; including daytime and low visibility condition use;
Bidder shall provide DECLARATION OF CONFORMITY from relevant accredited laboratory, that offered light fixtures comply to EASA and ICAO requirements, separate for each function type of lights (inset taxiway centre line lights, inset stop bar lights, elevated stop bar lights, taxiway edge lights, runway guard lights).
- ICAO Annex 14, part I, chapter 5 - lights
- FAA AC 150/5345-46; for material, construction performance, testing, light beams according to EASA and ICAO
- requirements of FAA Engineering brief 67 in following fields shall be met:
- accelerated fixture life test (burn-in test);
- implemented overvoltage / surge protection minimum C2 category (combination wave 1,2/50µs - 8/20 µs, peak voltage 10 000V, peak current 5 000A); galvanic insulation from secondary circuit shall provide additional protection against voltage surge;
- user shall not see light flickering at any current setting;
- delivered light fixtures shall be without additional heating ("arctic kit");
- minimum warranties 4 years;
- internal electronic supervision of light electronics shall not trigger "fail open" condition or light fixture shall be without such supervision, except where such supervision is explicitly required in BQ ("taxiway lead on lights", stop bar lights, runway guard lights) due single lamp control and monitoring thru "fail open" method (secondary circuit shows "open circuit" in case of light fixture failure or under performance); such "fail open" mechanism shall not be triggered due vibrations or overcurrent in primary circuit;
- light fixtures shall have modular design, with simple replacement procedures;
- electronics shall be encapsulated in water protective coating;
- light fixture shall be directly fed from the isolating transformer, separate power converters shall not be allowed;
- light intensity output shall be dimmable, similar to halogen light bulb output (Aerodrome design manual part 5, Electrical systems); in case of higher than 6,6 A, light output will remain stable and equal to output at nominal 6,6A;
- no visible flickering of light at any intensity step;
- if light fixture is powered by serial transformer with higher power rating than required by light fixture, then there will be no reduction in light fixture lifespan or increased light output;
- light fixtures shall have useful lifetime at least 48000 hours, near end of this time light output will still comply EASA / ICAO requirements;
0
- light fixture shall be powered thru serial circuit powered by any type of CCR (FAA AC 150/5345-10, IEC 61822) with nominal current 6,6A, 5 steps, 50 Hz
- all components of light fixture shall permanently resist the temperatures encountered during the normal operation of the fixture at full intensity under maximum ambient temperature;
- spare parts for offered light fixtures shall be available at least 10 years.
0
Inset light fixtures:
- nominal diameter 8";
- housing aluminum type;
- light fixture shall be max. 6,35 mm above surface (FAA inset lights, style 3);
- protective level at least IP 67, all fastenings are stainless steel;
- part of offer is also gasket between inset light and shallow base, gasket shall remain flexible and functional for longer time of use - longer than expected light fixture service interval; inside of shallow base shall be dry ("dry type of installation").
- offered inset taxiway centre line lights with different optical requirements, including inset intermediate holding position lights, shall be part of same product family (interchangable parts - optical lenses, filters excluded;
- succesfull bidder shall deliver lights and other equipment for LOT 2 till August 1st 2023
General logic for inset lights:
- wide beam on straight sections (bigger displacement of cockpit from center line); straight opening for light beam on housing;
- wide beam with toe-in on curved sections (bigger displacement of cockpit from center line); toe in opening for light beam on housing; exact color coding shall be done with successful bidder due different coding structures
0
Elevated light fixtures:
- elevated lights shall have separate column and breakable coupling;
- elevated light housing (base plate, coupling, etc.) shall be painted in aviation yellow color;
- elevated lights shall be mounted on L-867 base extensions;
- between base plate and L867 extension shall be installed gasket, gasket is part of offered equipment, base extension is not included in offer;
- elevated stop bar lights shall have higher light intensity;
- runway guard lights shall be used also during day time, higher light intensity required;
0
Shallow bases for for inset light fixtures:
- nominal diameter 8";
- aluminum type of material;
- side entry for wires, at installation on site will be used 2 or 4 wires AWG 10 for secondary circuit; protective earth wire shall be connected from outside of shallow base, crossing of wires from outside base into inside of base shall be water tight; at installation time on site shall be on shallow base wires crimped (connected) new wires installed from light base location to manhole by contractor for electrical works;
- metric threads, holes for bolts shall not be thru base wall (some shallow bases have option to use longer bolts, which goes thru base wall);
- bolts shall be stainless steel type (not coated);
- between light fixture and shallow base shall be gasket -> "dry type" of installation, gasket is part of offer; gasket shall remain flexible and remain functional after longer use (not became stiff);
- shallow base depth and inside curvatures of base shall allow installation of light fixtures from different manufacturers (general type of shallow base, deeper) ;
- all fastening screws inside shallow base shall be stainless steel;
0
Serial transformers:
- required power should be calculated by bidder, approx. max. distance from pit (installed transformer) to light shall be up to 45 m (AWG 10 secondary wires), secondary circuit shall be done on site by contractor for electrical works;
- stop bar lights (inset, elevated), runway guard lights, taxiway centre line lights after stop bar (lead on lights, 6 pcs, 2 plugs) shall be controlled by single lamp control elements, add sufficient power reserve at selecting transformer power. Single lamp control elements - separate elements - are not part of tender
- serial transformer shall be equipped with grounding terminal;
- minimum power for serial transformer shall be 30/45 W, please unify power in reasonable amount of different types of transformers.
0
General requirements for cables and connectors:
- bidder shall provide techical documentation for offered cables and connectors; offered primary cables and primary connectors shall fulfill required tehnical demands. Leakage current (insulation measurement with leakage current) shall be at least 7 times lower then allowed by leakage method.
- succesfull bidder shall deliver equipment for LOT 1 till August 1st 2023

## CABLES TWY J
Fraport Slovenija, d.o.o.
LOT1: Delivery of cables, connectors for the new taxiway TWY J and renovation of one section of taxiway TWY A
PRIMARY CABLES
item no. |  | item | unit | amount | price per unit | value
1 | . | Primary circuit cable 1x6mm2, 5kV, class 2 stranded copper conductor, 7 strands, XLPE insulation, min. 2,3 mm thick, semi-conducting tape on top of XLPE insulation, shielded - coper wire braid; PE outer sheath min. thickness 1,6 mm; overall cable diameter approx. 11,5-13 mm. Cable complying adopted FAA AC150/5345-7F (L-824), IEC60228; conductor resistance per km max. 3,11 Ohm, Successful routine test at 35 kV DC for 15 minutes, insulation resistance (sample 1000 ft) higher than 2220 Ohmkm at 15,6 deg.C;
Cable properties: abrasion resistant, oil resistant, UV resistant, deicer fluid resistant (FR/KAc), halogen free, service temperature -40 to +85 deg. C for nominal current 6,6A, minimal laying temperature -10 deg.C, minimal bending radius 12x outer diameter.
Expected electrical characteristic: C' = 150 nF/km; L' = 200 µH/km; Insulation resistance G' >= 1000 MOhm/km; Characteristic Impedance: Zc = 36 Ohm (for f >1 MHz); Attenuation dB/km (+/-15 %): 100 kHz: 2.8; 125 kHz: 3.2 ; 150 kHz: 3.5; 200 kHz: 4.0.
Eupen, SXC4E, Type C, copper wire braid screened, 5 kV
|  |  | m1 | 44000 |  | 0
|  | Summ - TWY J CABLES |  |  |  | 0

## Connectors TWY J
Fraport Slovenija, d.o.o.
LOT1: Delivery of cables, connectors for the new taxiway TWY J and renovation of one section of taxiway TWY A
PRIMARY CONNECTORS
item no. |  | item | unit | amount | price per unit | value
1 | . | Primary connector kit - set of male and female connector, for 1 conductor, up to 25A, up to 5 kV, field mounting, according to FAA AC/5345-26C L823, TYPE I, Class B, style 3 / 10, complying also ICAO Annex 14. Housing of connector is after installation on cable filled with special insulation resin. Connector shall have attached wire for connecting cable shield. Connector will be mounted on primary cable approx. outer diameter 11,5 - 13 mm.
Eupen, Connector kit FAA L-823, CKE 52
|  |  | set | 280 |  | 0
|  | Summ - TWY J PRIM. CONNECTORS |  |  |  | 0

## Light fixtures TWY J
Fraport Slovenija, d.o.o.
LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A
TWY J LIGHT FIXTURES
item no. |  | item | unit | amount | price per unit | value
1 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GG/P1) |  |  |  |  | W/GG/P1
|  |  | pcs | 4 |  | 0
2 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 4 |  | 0
3 |  | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#1). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 4 |  | 0
4 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Separate plug for each side. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. (Graphics: W/GG/P2) |  |  |  |  | W/GG/P2
|  |  | pcs | 3 |  | 0
5 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 3 |  | 0
6 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#4). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
7 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / yellow color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GY/P1) |  |  |  |  | W/GY/P1
|  |  | pcs | 1 |  | 0
8 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 1 |  | 0
9 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#7). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 1 |  | 0
10 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / yellow color of light. Separate plug for each side. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. (Graphics: W/GY/P2) |  |  |  |  | W/GY/P2
|  |  | pcs | 3 |  | 0
11 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 3 |  | 0
12 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#10). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
13 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to Annex 14, figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GG/P1) |  |  |  |  | C/GG/P1
|  |  | pcs | 12 |  | 0
14 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 12 |  | 0
15 |  | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#13). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 24 |  | 0
16 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / yellow color of light. Common plug for both sides. Light distribution according to Annex 14, Figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GY/P1) |  |  |  |  | C/GY/P1
|  |  | pcs | 5 |  | 0
17 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 5 |  | 0
18 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#16). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 5 |  | 0
19 | . | Stop bar inset light, 8" nominal diameter, housing for straight section / wide beam, CAT III, red / blank color of light. Plug for one side. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.730, inset light, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light / stop bar light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. (Graphics: W/R/P1) |  |  |  |  | W/R/P1
|  |  | pcs | 12 |  | 0
20 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 12 |  | 0
21 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#19). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 12 |  | 0
22 | . | Elevated taxiway edge light, overall height (from including base plate to top of the light) 48-52cm, omnidirectional, blue color of light. Single plug. Breakable coupling has to be separate item from column. Aviation yellow color of housing (column, breakable coupling ...). 1,5 inch nominal diameter for breakable coupling connected to base plate 12" for non load bearing deep base (L-867). Including base plate and gasket between base plate and base (base is not part of offer). Light has outer blue glass. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.720, mechanically complying FAA AC 150/5345-46, elevated taxiway edge light. |  |  |  |  | elevated edge light
|  |  | pcs | 22 |  | 0
23 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#22). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose. Suggested standard 30/45W.
|  |  | pcs | 22 |  | 0
24 | . | Elevated stop bar light, overall height (from including base plate to top of the light) 48-52cm, omnidirectional, red color of light. Single plug. Breakable coupling has to be separate item from column. Aviation yellow color of housing (column, breakable coupling ...). 1,5 inch nominal diameter for breakable coupling connected to base plate 12" for non load bearing deep base (L-867). Including base plate and gasket between base plate and base (base is not part of offer). Light distribution according to ICAO Annex 14, Figure A2-17 or EASA, Figure U-21. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.730, mechanically complying FAA AC 150/5345-46, elevated stop bar light. Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. |  |  |  |  | elevated stop bar light
|  |  | pcs | 4 |  | 0
25 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#24). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 4 |  | 0
26 | . | Elevated Runway guard light, high intensity, yellow color of light, LED type, overall height (from including base plate to top of the light) up to 65 cm. Single plug. Breakable coupling has to be separate item from column. Aviation yellow color of housing (column, breakable coupling ...). 2 inch nominal diameter for breakable coupling connected to base plate 12" for non load bearing deep base (L-867). Including base plate. Light has outer blue glass, automatically heated when temperatures below or near zero degree Celsius. Light distribution according to ICAO Annex 14, Figure A2-25 or EASA, Figure U-28. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.745, configuration A, mechanically complying FAA AC 150/5345-46, elevated runway guard light. |  |  |  |  | elevated RGL
|  |  | pcs | 2 |  | 0
27 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#26). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 2 |  | 0
26 | . | Male connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 4, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 124 |  | 0
27 | . | Female connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 11, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 40 |  | 0
|  | Summ - TWY J - lights |  |  |  | 0

## Light fixtures TWY A
Fraport Slovenija, d.o.o.
LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A
TWY A LIGHT FIXTURES
item no. |  | item | unit | amount | price per unit | value
1 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GG/P1) |  |  |  |  | W/GG/P1
|  |  | pcs | 46 |  | 0
2 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 46 |  | 0
3 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#1). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 46 |  | 0
4 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / yellow color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GY/P1) |  |  |  |  | W/GY/P1
|  |  | pcs | 3 |  | 0
5 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 3 |  | 0
6 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#4). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 3 |  | 0
7 | . | Taxiway intermediate holding position, 8" nominal diameter, housing for straight section / wide beam, CAT III, yellow color of light / blank . Single plug . Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.735, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/YX/P1) |  |  |  |  | W/YX/P1
|  |  | pcs | 9 |  | 0
8 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 9 |  | 0
9 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#7). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 18 |  | 0
10 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to Annex 14, figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GG/P1) |  |  |  |  | C/GG/P1
|  |  | pcs | 22 |  | 0
11 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 22 |  | 0
12 |  | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#10). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 44 |  | 0
13 | . | Male connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 4, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 111 |  | 0
|  | Summ - TWY A - lights |  |  |  | 0

## Light fixtures TWY M
Fraport Slovenija, d.o.o.
LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A
TWY M LIGHT FIXTURES
item no. |  | item | unit | amount | price per unit | value
1 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GG/P1) |  |  |  |  | W/GG/P1
|  |  | pcs | 1 |  | 0
2 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 1 |  | 0
3 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#1). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 1 |  | 0
4 | . | Taxiway intermediate holding position, 8" nominal diameter, housing for straight section / wide beam, CAT III, yellow color of light / blank . Single plug . Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.735, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/YX/P1) |  |  |  |  | W/YX/P1
|  |  | pcs | 3 |  | 0
5 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 3 |  | 0
6 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#4). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
7 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to Annex 14, figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GG/P1) |  |  |  |  | C/GG/P1
|  |  | pcs | 8 |  | 0
8 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 8 |  | 0
9 |  | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#7). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 16 |  | 0
10 | . | Male connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 4, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 23 |  | 0
|  | Summ - TWY M - lights |  |  |  | 0

## Light fixtures apron
Fraport Slovenija, d.o.o.
LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A
APRON BEFORE TWY M LIGHT FIXTURES
item no. |  | item | unit | amount | price per unit | value
1 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GG/P1) |  |  |  |  | W/GG/P1
|  |  | pcs | 9 |  | 0
2 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 9 |  | 0
3 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#1). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 9 |  | 0
4 | . | Taxiway intermediate holding position, 8" nominal diameter, housing for straight section / wide beam, CAT III, yellow color of light / blank . Single plug . Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.735, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/YX/P1) |  |  |  |  | W/YX/P1
|  |  | pcs | 3 |  | 0
5 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 3 |  | 0
6 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#4). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
7 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to Annex 14, figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GG/P1) |  |  |  |  | C/GG/P1
|  |  | pcs | 3 |  | 0
8 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 3 |  | 0
9 |  | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#7). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
10 | . | Male connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 4, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 21 |  | 0
|  | Summ - apron lights before TWY M - lights |  |  |  | 0

## Light fixtures spare parts
Fraport Slovenija, d.o.o.
LOT 2: Delivery of AGL lights for the new taxiway TWY J and renovation of one section of taxiway TWY A
LIGHT FIXTURES - spare parts
item no. |  | item | unit | amount | price per unit | value
1 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GG/P1) |  |  |  |  | W/GG/P1
|  |  | pcs | 15 |  | 0
2 | . | Shallow base, for above specified light, nominal diameter 8"; 2 wires side entry, dry type.
|  |  | pcs | 15 |  | 0
3 |  | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#1). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 15 |  | 0
4 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / green color of light. Separate plug for each side. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. (Graphics: W/GG/P2) |  |  |  |  | W/GG/P2
|  |  | pcs | 3 |  | 0
5 | . | Shallow base, for above specified light, nominal diameter 8"; double side entry, each 2 wires, dry type.
|  |  | pcs | 10 |  | 0
6 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#4). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
7 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / yellow color of light. Common plug for both sides. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: W/GY/P1) |  |  |  |  | W/GY/P1
|  |  | pcs | 4 |  | 0
8 | . | Taxiway centre line light, 8" nominal diameter, housing for straight section / wide beam, CAT III, green / yellow color of light. Separate plug for each side. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. (Graphics: W/GY/P2) |  |  |  |  | W/GY/P2
|  |  | pcs | 3 |  | 0
9 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / green color of light. Common plug for both sides. Light distribution according to Annex 14, figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GG/P1) |  |  |  |  | C/GG/P1
|  |  | pcs | 10 |  | 0
10 | . | Taxiway centre line light, 8" nominal diameter, housing for curved section (15,75 degree toe in) / wide beam, CAT III, green / yellow color of light. Common plug for both sides. Light distribution according to Annex 14, Figure A2-14 or EASA, Figure U-18. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.710, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light. Exact selection (which side of light fixture will have yellow output) shall be determined after bidding process, because each producer has own light product coding system. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). (Graphics: C/GY/P1) |  |  |  |  | C/GY/P1
|  |  | pcs | 5 |  | 0
11 | . | Stop bar inset light, 8" nominal diameter, housing for straight section / wide beam, CAT III, red / blank color of light. Plug for one side. Light distribution according to ICAO Annex 14, Figure A2-12 or EASA, Figure U-16. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.730, inset light, mechanically complying FAA AC 150/5345-46, in-pavement taxiway centre line light / stop bar light. Fixture elevation above ground max. 6,35 mm (low protrusion style 3). Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. (Graphics: W/R/P1) |  |  |  |  | W/R/P1
|  |  | pcs | 12 |  | 0
12 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#11). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 6 |  | 0
13 | . | Elevated taxiway edge light, overall height (from including base plate to top of the light) 48-52cm, omnidirectional, blue color of light. Single plug. Breakable coupling has to be separate item from column. Aviation yellow color of housing (column, breakable coupling ...). 1,5 inch nominal diameter for breakable coupling connected to base plate 12" for non load bearing deep base (L-867). Including base plate and gasket between base plate and base (base is not part of offer). Light has outer blue glass. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.720, mechanically complying FAA AC 150/5345-46, elevated taxiway edge light. |  |  |  |  | elevated edge light
|  |  | pcs | 10 |  | 0
14 | . | Elevated stop bar light, overall height (from including base plate to top of the light) 48-52cm, omnidirectional, red color of light. Single plug. Breakable coupling has to be separate item from column. Aviation yellow color of housing (column, breakable coupling ...). 1,5 inch nominal diameter for breakable coupling connected to base plate 12" for non load bearing deep base (L-867). Including base plate and gasket between base plate and base (base is not part of offer). Light distribution according to ICAO Annex 14, Figure A2-17 or EASA, Figure U-21. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.730, mechanically complying FAA AC 150/5345-46, elevated stop bar light. Light fixture shall have "fail open" feature, not sensitive to overcurrent or vibrations. |  |  |  |  | elevated stop bar light
|  |  | pcs | 2 |  | 0
15 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#14). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 2 |  | 0
16 | . | Elevated Runway guard light, high intensity, yellow color of light, LED type, overall height (from including base plate to top of the light) up to 65 cm. Single plug. Breakable coupling has to be separate item from column. Aviation yellow color of housing (column, breakable coupling ...). 2 inch nominal diameter for breakable coupling connected to base plate 12" for non load bearing deep base (L-867). Including base plate. Light has outer blue glass, automatically heated when temperatures below or near zero degree Celsius. Light distribution according to ICAO Annex 14, Figure A2-25 or EASA, Figure U-28. Complying: ICAO Annex 14, EASA, CS ADR-DSN.M.745, configuration A, mechanically complying FAA AC 150/5345-46, elevated runway guard light. |  |  |  |  | elevated RGL
|  |  | pcs | 2 |  | 0
17 | . | Serial transformer for use in airport light circuit, 6,6A / 6,6A; 50 Hz, according to FAA AC 150/5345-47 L-831 for light from position above (#16). Approx. distance between light and transformer (AWG10 wire): up to 45m, for power calculation purpose.
|  |  | pcs | 2 |  | 0
18 | . | Male connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 4, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 20 |  | 0
19 | . | Female connector for secondary light circuit , field montage, complying FAA AC/5345-26C L823, TYPE II, Class B, style 11, for connecting 2 wires AWG 10 (outside overall diameter approx. 4,9 mm).
|  |  | pcs | 10 |  | 0
|  | Summ - light fixtures - spare parts |  |  |  | 0