TECHNICAL SPECIFICATION FOR THE ORDER FOR THE

SUPPLY OF HANGER TUBES FOR RH 1

Content:

1	GENERAL	3

2	THE CONTENT OF THE CONTRACT	3

2.1	SUPPLY OF HANGER TUBES	3

2.1.1	Requirements for ordering hanger tubes, holders, and barriers	3

2.1.2	Warranties:	5

2.1.3	Supply	6

2.1.4	Attached drawings or sketches	6

GENERAL

On the existing Unit 6 installed in the Šoštanj power plant since 2015, we intend to carry out a partial replacement of the existing hanger tubes on Reheater 1 (RH1). For this purpose, TEŠ is tendering a public contract for the supply of hanger tubes.

THE CONTENT OF THE CONTRACT

SUPPLY OF HANGER TUBES

Scope of supply is 132 pcs of Hanger tubes in accordance with attached drawing No. STJ-06-B---00012-BE-016_02_Hanger tube supporting lugs_21-04-2011 – position RH1 and drawing No. STJ-06-B-HAJ1000242-BE-002_03-RH1 - heating surface-24-03-2011

Part list (dwg. STJ-06-B---00012-BE-016):

| Pos | Quan. | Designation | Dimension | Length[mm] | Material | Material Standard | Certificate |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 132 | Tube | OD 48.3x11.0 | 3530 | 7CrMoVTiB10-10 (Wr.No. 1.7378) | 10216-2 TC2 | 3.2 in acc to EN 10204 |
| 2 | 528 | Plate | 50 x 25 x 6 |  | X10CrAlSi7 (Wr.No. 1.4713) | EN 10095 | 3.1 in acc to EN 10204 |
| 3 | 6864 | Barrier | 35 x 20 x 6 |  | X10CrAlSi7 (Wr.No. 1.4713) | EN 10095 | 3.1 in acc to EN 10204 |
| 4 | 6864 | Supporting lug | 66 x 40 x 6 |  | X10CrAlSi7 (Wr.No. 1.4713) | EN 10095 | 3.1 in acc to EN 10204 |

Requirements for ordering hanger tubes, holders, and barriers

- Tubes

  - shall be delivered in acc. to Pressure equipment Directive with tensile test at elevated temperature 550°C, Impact test and microsection. Inspection certificate shall be issued/confirmed by PED Notified Body 
The length of supplied hanger tubes must be min 3530 mm (additional length of 50 mm on each side – see Dwg. STJ-06-B-HAJ1000242-BE-002) with beveled ends (30°) with root face of 1,6 mm closed with plastic caps.

- Hanger tubes

  - Pos. 3 Barrier shall be delivered without welding on pos. 2 and 4.

  - Marking transfer shall be made on all supplied parts, tube marking shall be confirmed by NoBo on each tube.

  - Hanger tube manufacturing company shall be certified in acc. to EN ISO 3834-2, welding procedure shall be made in acc. to PED and EN ISO 15614-1, welders shall be certified in acc. to PED and EN ISO 9606-1. Manufacturing shall follow EN 12952 standard series.

- The customer reserves the right to carry out inspections at the pipe manufacturer (iron works) as well as at the company to produce hanger tubes.

- All hanger tubes must be corrosion protected (min 50 microns).

Picture 1: delivery length of hanger tubes (look red dimension)

barriers

Plates

Picture 2 and 3: Movement limiters – barriers

Warranties:

The quality and dimensions of supplied tubes must be according to the order.

The warranty period for supplied tubes must be at least one year.

The customer reserves his rights that taking over of delivery will be performed only after successful performed entrance control.

The supplier must ensure replacement of all non-conform hanger tubes, within one month after written notice, at its own cost.

Supplier shall provide followed documents:

- With offer:

  - ISO 9001 certificate for pipe manufacturer

  - EN ISO 3834-2 certificate for Hanger tube manufacturer

- 1 month after Contract:

  - EN ISO 15614-1 certificates for welding 7CrMoVTiB10-10 with X10CrAlSi7

  - Welders’ certificates in acc. to PED and EN ISO 9606-1

  - PWHT procedure

  - Inspection and test plan

  - Time schedule for material delivery and manufacturing

- 14 days before agreed witness or hold point notification to Employer.

Supply

The deadline for delivery of tubes is the end of January 2025.

Attached drawings, sketches and documents

- 1.4831500 242 - 3111 Welding list

- STJ-06-B---00012-BE-016_02_Hanger tube supporting lugs_21-04-2011

- STJ-06-B-HAJ1000242-BE-002_03-RH1 - heating surface-24-03-2011STJ

- 06-B-HAJ-1000242-DE-113 RH1 Tube coils supporting parts

Footnotes:

The client allows the next following option:

If the provider, due to the market condition, will have to purchase the entire batch of the pipes - 7CrMoVTiB10-10; Ø48.3 x 11mm (to produce hanger tubes), he must state this in in offer and fill order specification under option 2. The remaining tubes must be handed over to the client.