## SILO
LOT 2 – Repository facilities
A.1- 1. SILO – DIAPHRAGM AND EXCAVATION
RECAPITULATION OF COSTS
Position | Description |  |  |  | Value (EUR)
1.1 | PRIMARY PROTECTION OF THE EXCAVATION (DIAPHRAGM) |  |  |  | 0
1.2 | SILO – construction pit
1.2.1 | SURVEYING WORK |  |  |  | 0
1.2.2 | EARTHWORKS |  |  |  | 0
1.2.3 | MISCELLANEOUS WORKS |  |  |  | 0
1.2.4 | DRAINAGE OF WATER FROM THE CONSTRUCTION SITE |  |  |  | 0
0
| Contingency 10% |  |  |  | 0
| TOTAL: |  |  |  | 0
Position | Description | Unit | Quantity | Price | Value (EUR)
1.1 | PRIMARY PROTECTION OF THE CONSTRUCTION PIT EXCAVATION – THICK-WALLED CONCRETE DIAPHRAGM OF CYLINDRICAL SHAPE
DESCRIPTION AND NOTES
Basic dimensions of a thick-walled concrete diaphragm: The diaphragm is cylindrical with an internal diameter of 29.3 m, a height of 64.4 m (153.40-89 m a.s.l.) and a thickness of 1.5 m. It will be constructed from 7.4 m wide primary panels and 2.8 m wide secondary panels. The panels will be joined by cutting the secondary panels approximately 30 cm into the primary panels. The volume of the diaphragm is 8,902 m3. The area at the mean diameter is 6,272 m2. The volume of the connecting beam at the top of the diaphragm is 558 m3.
The uniform prices for the construction of the diaphragm must include all labour, machinery, construction supervision and monitoring costs, with the preparation of reports in accordance with the implementation documentation, the special technical conditions and the general technical conditions.
The following scope is foreseen for the construction of the underground wall (diaphragm) in accordance with the project documentation and the special technical conditions: – mobilisation (transport to the site) of all necessary equipment (heavy bentonite leachate treatment plant, separators, settling tanks, crane for fitting, milling machine, etc.), – construction site layout – removal of the construction site – execution of the introduction works (excavation, formwork, reinforcement, concrete, backfill) – excavation of primary and secondary panels using the hydrofracturing principle in the presence of heavy bentonite mud, with continuous monitoring, – panel reinforcement in combination with metal boxes welded to the reinforcement cage and protection of the metal boxes prior to being inserted into the panel (metal boxes are provided to ensure anti-shear grooves) – contractor concreting of panels – excavation of a construction pit for the construction of a connecting beam – pre-preparation of the surface for the connecting beam – construction of the connecting beam (formwork, reinforcement, concrete)
– backfilling on the outside of the beam – Correction of the inner surface of the diaphragm during the excavation phase of the silo pit (local removal of part of the diaphragm wall due to inward deflections, milling of the diaphragm surface, shotcrete as a substrate for the installation of the waterproofing liner).
Working plateau
The top of the guide wall shall be considered as the initial working level from which dredging operations shall be carried out.
Disposal
Disposal means the loading, removal, recycling or final storage and/or disposal of construction waste.
The following activities are included in the prices:
Contractor's technical report
The contractor shall submit to the contracting authority, prior to the commencement of the works, a technical report (method statement) on the execution of the works, including all prescribed measures. Failure to do so may result in cancellation of the contract by the contracting authority. The technical report includes: – the method and technology of execution, – the timing of the works (schedule), – ensuring position control and accuracy of execution, – measures to prevent uplift or settlement (e.g. due to relief drilling).
Protocol
For each concrete wall (diaphragm), the contractor shall provide the contracting authority with an inspection sheet containing the following information: – number according to the site plan, – start and end of construction procedure, – the length of obstacles (materials, e.g. walls) crossed, – special events, with date and time.
Spoil dredging (spoil cut)
The part of the excavation between the top edge of the guide wall and the bottom edge of the element to which the concrete diaphragm is attached is considered to be spoil. In any case, the spoil is covered by the lump sum price. The price also includes the filling of the empty space after the diaphragm has been made, including all transport.
Connecting beam at the top of the diaphragm
The concrete diaphragm shall be concreted to a height such that the design strength of the concrete is achieved at the required height of the concrete diaphragm after removal of the top low quality concrete. It should be noted that the top of the diaphragm 1.7 m high is a connecting beam, so the concreting of the panels ends approximately 1.6 m below the working platform. Consideration should be given to partial removal of the upper poor quality concrete with a minimum thickness of 0.5 m prior to construction of the connecting beam.
The cost of removing poor quality concrete before it reaches full strength, including free reinforcement to continue concreting, is included in the prices of the items in this schedule.
The following activities are included in the unit price (in addition to ancillary activities): – keeping a record of ongoing geological surveys, – a technical report; – backfilling, spreading and grading of excavated material for use on the construction site, – Any deviation from the tolerances specified in the design for which the contractor is responsible, will be rejected, – miscellaneous formwork required for excavations not included in the project, – disposal of excavated material and other waste (e.g. suspension) to a permanent disposal site to be agreed with the supervisor or investor
Measurements and accounting rules:
Tendering and accounting follows the vertical section. Activities are mapped from elevation zero (working plateau elevation 153.40 m a.s.l.) to the prescribed depth.
Diaphragm excavation shall be charged by m2 of excavated diaphragm, measured in the axis of designed diaphragm and includes all works, including spoil cutting, milling, excavation in all categories of materials and milling of primary panels and excavations.
Special site preparation for the concrete diaphragm (e.g. working plateau, equipment set-up, protective scaffolding) according to the contractor's site organisation plan. The contractor shall deliver the site plan to the contracting authority 14 days after the signing of the contract. A reinforced working plateau has been prepared for the organisation of the site.
Only aggregates complying with the requirements of the NRVB---6G1010 Primary Silo Lining (Diaphragm) Technical Specification may be used for the production of concretes to be permanently installed in the diaphragm area and the diaphragm itself. The use of these aggregates should be included in the unit price of concrete.
1.1.1 | Construction site preparation for the concrete diaphragm | flat rate | 1 |  | 0
Preparation and maintenance
1.1.2 | Clearing the construction site for the concrete diaphragm
| Cleaning and restoration, including removal of excess soil. | flat rate | 1 |  | 0
1.1.3 | Equipment and machinery for the execution of the concrete diaphragm: preparation, access and removal, erection and dismantling, in the required numbers and in the required manner, including relocation within the construction site area and/or construction site sections. When arranging the equipment on site, it must be taken into account that a free area of approx. 5 m must be left on the outside of the diaphragm for the construction of the connecting beam at the top of the diaphragm.
1.1.4 | Equipment and machinery for the construction of concrete diaphragm | flat rate | 1 |  | 0
Choice of equipment: The contractor shall be equipped with a water jet cutting machine for the excavation of the diaphragm panels. The (water jet cutting machine) machinery must be equipped, inter alia, with all the necessary devices for monitoring the position of the milling machine and for correcting it in the event of deviations. The contractor must have all the necessary machinery and equipment for the handling of the reinforcement for the assembly of the heavy reinforcement cages, as well as for their installation on site (the weight of the reinforcement cages (3) for the primary and secondary slabs is approximately 74 t and 32 t, respectivelly); the contractor must have all the necessary machinery and equipment for the execution and handling of the bentonite mud, as well as all the necessary machinery for the proper execution of the tremie method of concreting.
1.1.5 | Pre-work – surveying work
1.1.5.1 | Setting out the lead diaphragm wall | set | 1 |  | 0
1.1.6 | Complete construction of reinforced concrete lead wall including formwork, concrete, reinforcement and any connections, depending on the type of soil, regardless of dimensions, including excavation, temporary storage, backfilling of the completed wall in layers to the required density and stiffness. Calculation based on the length of the lead wall measured along the axis of the wall. The price must also include the design of the Detailed design project for the lead wall.
1.1.6.1 | Lead wall for concrete diaphragm
| – internal wall | m | 92 |  | 0
| – external wall | m | 103 |  | 0
1.1.7 | Complete removal of the lead wall structure, including excavation for the connecting beam and removal of the removed material to the municipal landfill. Prior to excavation, the remaining amount of bentonite mud has to be removed. Calculation based on the length of the lead wall measured along the axis of the wall.
1.1.7.1 | Demolition and removal of the lead wall (inner and outer part) | m | 195 |  | 0
1.1.8 | Excavation for a 1.5 m thick concrete diaphragm using the principle of primary and secondary panels with a milling machine (water jet cutting machine) with a constant supply of heavy bentonite mud for the purpose of maintaining the stability of the excavation. The primary panels, which are approximately 7.4 m wide, will be built in three stages. Secondary panels of 2.8 m width are to be made by cutting into the existing primary panels by approximately 0.3 m on each side. The continued presence of bentonite mud and the continued replenishment of lost mud must be considered. This area refers to the axis of the diaphragm. A total of 10 primary and 10 secondary panels are foreseen.
1.1.8.1 | Excavation for a concrete diaphragm 1.5 m thick and 64.40 m deep. The excavation will take place in alluvial soil (cat. III) to a depth of approximately 13 m and then in pre-consolidated silt (cat. IV); the excavation area for the primary and secondary panels is 6,569 m2.
1.1.8.1.1 | Primary panels | m2 | 4766 |  | 0
1.1.8.1.2 | Secondary panels (unit price shall also include concrete milling of existing panels) | m2 | 1803 |  | 0
1.1.9 | Supply and placement of concrete in the primary and secondary diaphragm panels using the principle of underwater (tremie) continuous concreting. A minimum of two tremies should be considered for primary panels and a minimum of one tremie for secondary panels.
1.1.9.1 | Concrete quality C35/45, XC3, PV-I, CL0,2 | m3 | 9900 |  | 0
1.1.10 | Construction of a 3.2 x 1.7 m connecting beam at the top of the diaphragm. The concreting of the diaphragm panels is completed 1.6 m below the working plateau. The bentonite mud must be pumped out prior to excavation. As part of the excavation, the retaining walls will also be removed.
1.1.10.1 | – excavation in cat. III soil with removal to a temporary landfill | m3 | 344 |  | 0
1.1.10.2 | – backfilling with material from the excavation with consolidation in layers up to a maximum thickness of 50 cm to the prescribed compaction and stiffness | m3 | 198 |  | 0
1.1.10.3 | – Removal of poor quality concrete at the top of the diaphragm (water jetting required) | m3 | 240 |  | 0
1.1.10.4 | – double-sided formwork of an arched wall with support | m2 | 697 |  | 0
1.1.10.5 | Supply and pouring of concrete in non-reinforced structures of cross section up to 0.15 m3/ m2/m; with all auxiliary parts and transport to site of pouring: ~ concrete C16/20 X0: concrete base under the connecting beam | m3 | 39 |  | 0
1.1.10.6 | Supply and placing of concrete in solid structures with a section greater than 0.30 m3/ m2- m1 – concrete of diaphragm connecting beam – concrete C35/45, XC3; Dmax 32 The concrete must be waterproof and laid in blocks in accordance with the technical specifications. | m3 | 559 |  | 0
1.1.10.7 | Supply, installation and bonding of medium complexity reinforcement in ribbed concrete steel of B500B quality, reinforcing bars φ > 14 mm. | kg | 173512 |  | 0
1.1.11 | Subsequent treatment of the surface of the concrete diaphragm, regardless of height, after excavation, cleaning according to the technology of the contractor, including any scaffolding, and removal of waste material. Charged by area worked. The work is carried out in stages as the silo pit is excavated.
1.1.11.1 | Cleaning of the concrete diaphragm surface and manual levelling of the surface by rebating sharp edges. | m2 | 4800 |  | 0
1.1.11.2 | Cleaning anti-shear grooves and rings with preparation of surface for laying waterproofing. Anti-shear rings on three levels with a total area of 550 m2, anti-shear grooves on three levels (60 pcs) with a total area of 225 m2 | m2 | 775 |  | 0
1.1.11.3 | Concrete diaphragm levelling (approx. 30% of the area) | m2 | 1440 |  | 0
Removal of excess concrete up to the design thickness or due to deviations of the panels from the design line, according to the requirements of the design (punching or cutting).
1.1.11.4 | Removal of concrete around shear rings and shear grooves. | m3 | 360 |  | 0
1.1.11.5 | Sprayed concrete on the diaphragm wall up to 10 cm thick, i.e. up to the theoretical outer line of the secondary lining. Cement consumption min. 300 kg/ m3, aggregate fraction 0-4 mm is foreseen. | m2 | 3392 |  | 0
1.1.11.6 | Injection moulding of the joints between the primary and secondary panels, using polyurethane or epoxy resins, etc.
1.1.11.6.1 | Drilling of holes in the reinforced concrete skeleton of the diaphragm panels; drilling at an angle to the panel contact to a depth of up to 2/3 of the panel thickness (estimate) | m | 900 |  | 0
1.1.11.6.2 | Conducting the injection process using approximately 20 kg of grout per well. | unit | 600 |  | 0
1.1.12 | Reinforcement for concrete diaphragm. Steel elements shall be installed in the reinforcement cages to provide anti-shear grooves. In the diaphragm, the bottom three rows are fitted with anti-shear rings and the top three rows are fitted with anti-shear grooves (60 pieces, 2.1 x 2 x 0.25 m). Amount of reinforcement based on reinforcement extract. As part of the technological design of the diaphragm, the contractor must prepare the most time-optimised assembly and installation of reinforcing cages, taking into account the space available for unfolding and the appropriate lifting equipment. The primary panel consists of three independent reinforcing cages, the outer two weighing 23 tonnes and the central one weighing 28 tonnes. The weight of the reinforcing cage in the secondary panel is 32 tonnes. The contractor shall also include in the unit price any ancillary work required for the installation of the reinforcing cages in the trench for the panels, such as surveyor's supervision or the possible construction of a template, and the spacers for the offset from the trench wall shall also be included in the unit price.
1.1.12.1 | Supply, installation and bonding of complex reinforcement in ribbed concrete steel of B500B quality, reinforcing bars φ > 14 mm including all ancillary reinforcement. | kg | 988164 |  | 0
1.1.12.2 | Supply, installation and bonding of complex reinforcement in ribbed concrete steel of B500B quality, reinforcing bars φ = 50 mm including all ancillary reinforcement. | kg | 164152 |  | 0
1.1.12.3 | Manufacture of steel elements to form the anti-shear grooves and their installation by welding into the reinforcing cages of each panel. The steel components are manufactured from S235JR structural steel.
| – elements type PL1 (60 pcs) | kg | 14166 |  | 0
| – elements type PL2 (30 pcs) | kg | 7599 |  | 0
| – elements type PL3 (60 pcs) | kg | 12300 |  | 0
| – elements type PL1 (30 pcs) | kg | 8865 |  | 0
1.1.13 | Filling of anti-shear grooves to facilitate later removal of concrete (e.g. Styrodur panels or as suggested by the contractor). | m2 | 900 |  | 0
1.1.14 | Measurement of the dimensions of each panel after the excavation of each panel has been completed, using the principle of an ultrasonic drilling monitor. The ultrasonic measurement is the basis for the 3D display of the finished diaphragm.
1.1.14.1 | Ultrasonic measurement of each panel after excavation using an ultrasonic device (such as the KODEN ultrasonic drilling monitor). | unit | 20 |  | 0
| TOTAL PRIMARY PROTECTION OF THE EXCAVATION |  |  |  | 0
1.2 | SILO – construction pit
1.2.1 | SURVEYING WORKS
NOTE:
All surveying work must be carried out in accordance with the provisions of the implementation documentation: Plan NRVB---7I/01 - Primary substructure Plan NRVB---6G1020 Secondary silo lining Plan NRVB---6G1806 Chapter 0 General technical conditions
1.2.1.1 | 3D laser scanning of each excavation step, including computer processing to create a 3D representation of the excavated diaphragm surface to identify areas for possible surface correction. | flat rate | 1 |  | 0
1.2.1.2 | Conducting geodetic surveys of individual points as part of the excavation steps, as required. | flat rate | 1 |  | 0
1.2.1.3 | Surveyor's supervision of the excavation (phasing) of the bottom arch of the foundation slab (spherical form) | flat rate | 1 |  | 0
| SURVEYING WORKS TOTAL |  |  |  | 0
1.2.2 | EARTHWORKS
Excavation of the silo pit
Note: All excavation work and transport of excavated material shall be accounted for on the basis of the volume of soil in the loosened state. All embankment works shall be accounted for by the volume of soil in the as-built condition. The excavated material is transported from the silo pit by means of a powerful tower crane using a suitable container with a capacity of approximately 6 m3. The price of the excavation also includes loading onto a means of transport and transport to a disposal site for a distance of up to 500 m, unloading, spreading and loose rolling with a bulldozer. The single price for the earthworks also includes the cost of constructing and maintaining a stairway for access to the earth works site for all phases of the earth works and for the duration of the earth works, including the construction of the foundation blocks for the secondary silo lining.
1.2.2.1 | Loading and removal of the separated material resulting from the excavation of the diaphragm panels and transport to a temporary disposal site up to 500 m away. | m3 | 10800 |  | 0
1.2.2.2 | Mechanical excavation of cat. III gravel material in the silo with loading and transport to a temporary disposal site. | m3 | 4567 |  | 0
1.2.2.3 | Mechanical excavation of cat. III gravel material under water in the silo and access shaft with loading and removal to a temporary disposal site. | m3 | 1957 |  | 0
1.2.2.4 | Mechanical excavation in the field cat. IV By milling or demolition by hydraulic breakers (consolidated silt) in the silo with loading and transport to a disposal site. Excavation by mining is not permitted. | m3 | 29105 |  | 0
1.2.2.5 | Loading, transport to temporary disposal site up to 500 m, unloading, spreading and light rolling with a bulldozer. | m3 | 47431 |  | 0
| GROUND WORKS TOTAL |  |  |  | 0
1.2.3 | MISCELLANEOUS WORKS
1.2.3.1 | Silo waterproofing
The silo is to be waterproofed with a 3 mm thick PVC membrane in combination with a geotextile as a mechanic protection, fixed to the primary lining (diaphragm) as well as to the underlying concrete of the silo base slab. The surface must be flat with no sharp edges. The price also takes into account the details of the foil around the pumping well pipes, the control piezometers and the pipe connection to the drainage shaft, as well as all other work necessary for the proper execution of the waterproofing (testing the watertightness of the welds, etc.) in accordance with the technical conditions in the report NRVB---7G1402. The working joints are sealed with external waterstop strips which divide the waterproofing area into individual closed watertight units, providing additional safety in the event of liner damage.
1.2.3.1.1 | Supply and installation of 3 mm thick PVC membrane. The membrane is spot welded to the pre-installed discs, which are used to attach the geotextile to the substrate. The liner is joined by welding. The use of 500 g/ m2 geotextile for mechanical protection is envisaged. The lump sum price also includes all penetrations and details such as insulation of shear grooves, passage of pipes through the membrane, membrane anchoring, repair of any penetrations due to the anchoring of the contractor's equipment, repair of any damage to the membrane during the execution of the works, etc. The UV protection of the membrane on exposed parts must also be included in the lump sum price. The calculation is based on the clear area of the membrane. | m2 | 6745 |  | 0
1.2.3.1.2 | Supply and installation of 3 mm thick PVC protective membrane. The membrane is laid over the base membrane and thermally welded to the flange of the waterstops. | m2 | 1000 |  | 0
1.2.3.1.3 | Supply and installation of 60 cm wide end waterstops at the working joints of the structure to be welded to the liner. | m | 1716 |  | 0
1.2.3.1.4 | Supply and installation of final (external) waterstops, approx. 32 cm wide, to be installed in the formwork prior to concreting, for the purpose of fixing the PVC sheeting on the outside of the secondary liner between levels 153 and 155.30 m above sea level. | m | 172 |  | 0
1.2.3.1.5 | Supply and installation of waterstops with epoxy adhesive bonded to the substrate for fixing the PVC membrane to the waterproofing finish details (shear dowels, silo top) – estimate. | m | 3000 |  | 0
| TOTAL WATERPROOFING |  |  |  | 0
1.2.3.2 | Drainage under the silo base
Any seepage water is drained through the primary arch from the drainage fins under the silo base to the drainage sump in the centre. The drainage system should be sealed by grouting after the silo has been constructed.
1.2.3.2.1 | Excavation of drainage troughs in soil cat. IV with removal of material to deposit site | m3 | 6 |  | 0
1.2.3.2.2 | Blowing out and cleaning the bottom of the silo excavation and drainage channels prior to the construction of the drains and underlying concrete. | m2 | 750 |  | 0
1.2.3.2.3 | Supply and installation of drainage backfill with gravel filter granulation 4 - 16 mm | m3 | 6 |  | 0
1.2.3.2.4 | Supply and installation of drainage pipes DN100 | m | 75 |  | 0
1.2.3.2.5 | Supply and installation of non-woven geotextiles over drainage troughs to protect against pouring of the underlying concrete | m2 | 120 |  | 0
1.2.3.2.6 | Supply and installation of PVC liner | m2 | 60 |  | 0
1.2.3.2.7 | Supply and installation of a dimpled membrane on the primary liner to drain any water that may seep through the primary liner. (estimate) | m | 300 |  | 0
| Total drainage under the base |  |  |  | 0
1.2.3.3 | Manufacture and removal of reinforced concrete slabs dim. 2 x 2 x 0.3 m in the centre of the silo for the initial wall and geodetic monitoring of the diaphragm panels and the installation of a tapping point in the centre of the slab. | unit | 1 |  | 0
| TOTAL MISCELLANEOUS WORKS |  |  |  | 0
1.2.4 | CONSTRUCTION SITE DEWATERING
NOTE
The pumping volumes and the system for the installation of the pumping stations shall be carried out in accordance with Plan NRVB---7I/01 and the PZI for the pumping and pressure relief control wells for the LILW facility (IRGO - 3009856). The lump sum prices include all costs for the design, installation, operation and removal of the pumping station system for all phases of the works, including the provision of autonomous power supply to the pumping stations.
a) To continuously ensure pumping and the functioning of the entire system of pumping from the excavation pit during the construction of the excavation pit and the silo’s secondary liner, the contractor must ensure a 24-hour watch at the construction site or an automatic alert system for faults in the pumping system and servicing staff that can begin the job of re-starting the pumps in less than two hours from the alert. Throughout the duration of pumping, the contractor must ensure an autonomous source of power supply for the pumps in case of power failure at the on-site transformer station. The contractor must ensure and maintain the silo pumping system throughout construction until a watertight roof is finished on the hall above the silo.
b) The contractor’s technical plan of pumping from the silo excavation pit and the silo drainage system must encompass all the work phases and event scenarios so that continuous and uninterrupted pumping from the excavation pit as well as drainage is ensured. Given the groundwater inflow projected in the design, the contractor must determine the appropriate capacity of pumps for the operation of the drainage system, the appropriate capacity of the pumps and pumping station for rainwater and process water pumping, and the dimensions of all pipelines and collecting vessels at the bottom and top of the silo. Provision must also be made for a system of draining pumped water through settlers and infiltration fields. Only clean water may be returned to infiltration fields. Before releasing pumped water into an infiltration field, its quality must be monitored by taking samples at least once a week.
c) The contractor’s unit price of pumping during secondary liner construction must include all works, material and equipment needed for the establishment, operation and maintenance of pumping stations. The unit price must also include a stand-by electric generator capable of covering the total power consumption of pumping, the cost of a 24-hour watch or an automatic fault alert system and servicing staff that ensures uninterrupted operation of the pumping system, the drainage of excess pumped water, the implementation of settlers and infiltration fields, and the monitoring of pumped water quality before its release into the infiltration field.
All the costs of pumping shall be included in the flat-rate unit price for the full duration of water pumping from the silo construction pit in the phase of secondary liner construction until the hall above the silo is covered with a watertight roof. If the deadline for the completion of works on the silo’s secondary liner or the hall above the silo is extended for reasons which the contracting authority is not responsible for, the contractor is not entitled to compensation due to the increased volume of work required to pump water from the silo construction pit.
1.2.4.1 | Pumping of drainage, rainwater and process water during excavation of the silo pit
1.2.4.1.1 | Pumping of drainage and rainwater to the surface from a storage tank with a capacity of at least 9 m3. Pumping is planned with submersible pumps with a capacity of approximately 25-30 l/s (37 kW), e.g. Flygt BS 2201 HT3-259. The collection tank and the riser (DN100 steel pipe) are successively adapted to the excavation steps and fixed in the diaphragm wall. | flat rate | 1 |  | 0
1.2.4.2 | Pumping of drainage water, rainwater and also process water during the construction of the foundation slab and the secondary lining of the silo.
1.2.4.2.1 | Pumping of drainage and rainwater to the surface from a storage tank with a capacity of at least 9 m3. Pumping is planned with submersible pumps with a capacity of approximately 25-30 l/s (37 kW), e.g. Flygt BS 2201 HT3-259. The collection tank is positioned approximately in the centre of the silo on the base plate at the silo inlet, while the riser (DN100 steel pipe) is fixed to the inlet structure. | flat rate | 1 |  | 0
| DRAINAGE TOTAL: |  |  |  | 0