## Recapitulation
Contractor: | ARAO, Vrbina 17, 8270 Krško
Facility: | Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | B.6_L2
B.6 TECHNICAL SECURITY SYSTEMS
PROJECT BILL OF QUANTITIES WITH PRELIMINARY MEASUREMENTS
RECAPITULATION
Amount
1. | Electricity supply and cable trays for the technical security system | 0
2. | Intruder alarm system | 0
3. | Access control system | 0
4. | Video surveillance system | 0
5. | Other works | 0
| Total value – excluding VAT: | 0
| Contingency (7%) | 0
| TOTAL TECHNICAL SECURITY SYSTEMS | 0

## 1. Electricity supply
Contractor: | ARAO, Vrbina 17, 8270 Krško
Facility: | Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
Position |  | Description of equipment or service | Unit | Quantity | Price per unit (€) | Value (€)
1. |  | Electricity supply and cable trays for the technical security system
Note: The types indicated are only intended as examples for the specification of technical characteristics and qualities. Equipment from other manufacturers of better or equivalent qualities and functionalities may also be supplied.
1.1 |  | Power cables
| 1. | Supply and installation of power cables and earthing cable, including labelling accessories, junction boxes, small fittings and connectors:
| 1.1 | FG70R 5x10 mm2 | m | 5 |  | 0
| 1.2 | NYM-J 3x1.5mm2 | m | 850 |  | 0
| 1.3 | NYM-J 3x2.5mm2 | m | 800 |  | 0
| 1.4 | NYM-J 3x4mm2 | m | 1300 |  | 0
| 1.5 | NYY-J 3x6mm2 | m | 700 |  | 0
| 1.5 | NYY-J 3x16mm2 | m | 150 |  | 0
1.2 |  | UNINTERRUPTIBLE POWER SUPPLY SYSTEM – UPS2
| 1. | Uninterruptible power supply (UPS) with rated power of 15kVA/15kW using on-line technology in accordance with EN62040-3 (VFI-SS-111, three-level IGBT converters), minimum autonomy of system 10 minutes at 75% load. The UPS must have a dual input mains (separate for the rectifier part and for the auxiliary network). | unit | 1 |  | 0
The UPS system must meet the following requirements:
Rated power 15 kVA/15 kW, output power factor 1.
Input voltage: 400V (3phase+N), voltage tolerance 240–480V.
Input frequency 50/60 Hz ± 10% Hz.
Input power factor ≥ 0.99
Input current distortion THDi <2%
Output voltage 3x400 V + N.
Output frequency 50 Hz ± 0.01% when network not present.
Output voltage tolerance ±1% for static loads, for dynamic loads in accordance with VFI-SS-111EN 62040-3.
Total harmonic voltage distortion with linear loads <1%, <5% for non-linear loads.
No reduction of operating power for consumers within the power factor range 0.9 inductive to 0.9 capacitive.
Inverter overload capacity: 125% for 10 minutes, 150% for 1 minute.
Built-in automatic bypass and manual maintenance bypass,
crest factor 3:1
Environment:
Working temperature 0°C to +40C° (from 15°C to 25°C for longest battery life).
Maximum relative humidity (non-condensing) 95%.
Sound level at 1m distance <53dBA
IP protection level – IP20
Management and communication: Advanced LCD touch screen with colour graphic display to read operating parameters on the device, Communication options for Modbus TCP, Modbus RTU, BACnet/IP.
Built-in SNMP/WEB communication interface for remote UPS monitoring and shutdown management of various operating systems, must be SSH compatible.
Built-in relay card to communicate main states of the UPS to the central control system (potential-free relay outputs).
UPS must be compatible with mobile applications that facilitate set-up via guided installation, checklists and user instructions.
Batteries:
Minimum operational autonomy 10min at 75% load.
Built in valve-regulated (VRLA) batteries of Long Life type as per EUROBAT 2015 (design life of 10–12 years), installed in a separate cabinet with protective elements.
Expert Battery System (EBS) to achieve maximum battery life through intelligent charging.
Compliance with standards:
CE certificate, safety standard SIST EN 62040-1-1, EN 60950-1, electromagnetic compatibility SIST EN 62040-2 (C3 category), technical specifications SIST EN62040-3.
The on-line UPS must guarantee a mean time between failures (MTBF) greater than 300,000 hours, officially attested.
The required UPS must be manufactured in Europe by a manufacturer holding valid ISO9001 and ISO14001 certification.
The equipment tenderer must operate in accordance with the ISO9001 standard, demonstrated by the corresponding valid certificate, and provide round-the-clock service 365 days of the year.
Supply of equipment to facility site, installation, connections to prepared installations, testing and start-up, user training, user instructions and maintenance instructions in the Slovene language, set.
1.3 |  | Electrical distribution board +GRU-TV
| 1. | Supply and installation of electrical distribution board for technical security systems power supply with UPS, of type e.g.: AE, Rittal, wall-mount enclosure, colour RAL 7035, type tested in accordance with SIST EN 60439-1,2. IP55 protection, dimensions (WxHxD): 800×1200×300mm, single door, with wiring and following equipment installed: | piece | 1 |  | 0
| 1.1 | 3-pole main switch, 80A, 690 V, AC, with door coupling rotary handle, Of type e.g.: PN1-80+NZM1-XTVDVR+NZM1/2-XV4+NZM1-XKA2, Eaton | piece | 1 |  | 0
| 1.2 | LED luminaire, 900lm, 4000K, 11W 100–240V, IP20, Of type e.g.: SZ 2500.200, Rittal | piece | 1 |  | 0
| 1.3 | Miniature circuit breaker, C, 3A, 1p, 10kA Of type e.g.: PL7-C3/1, Eaton | piece | 1 |  | 0
| 1.4 | Miniature circuit breaker, C, 4A, 1p, 10kA Of type e.g.: PL7-C4/1, Eaton | piece | 20 |  | 0
| 1.5 | Miniature circuit breaker, C, 6A, 1p, 10kA Of type e.g.: PL7-C6/1, Eaton | piece | 5 |  | 0
| 1.6 | Miniature circuit breaker, C, 10A, 1p, 10kA Of type e.g.: PL7-C10/1, Eaton | piece | 4 |  | 0
| 1.7 | Miniature circuit breaker, C, 16A, 1p, 10kA Of type e.g.: PL7-C16/1, Eaton | piece | 2 |  | 0
| 1.8 | Single-pole selector switch (1-0-2) to control lighting along the perimeter fence of the repository, 10A, for installation on enclosure door Of type e.g.: CG4 A210-600 FS2, Schrack | piece | 1 |  | 0
| 1.9 | Modular contactor, 4-pole, 25A, 230V, for mounting on DIN rail E.g. P/N BZ326461, Schrack | piece | 1 |  | 0
| 1.10 | Timer light relay with photocell/outside light sensor, 2-2000 lx, for mounting on DIN rail E.g. P/N BZ327731-A, Schrack | piece | 1 |  | 0
| 1.11 | N, PE busbar | piece | 1 |  | 0
| 1.12 | Terminal block, 4mm2 E.g. WDU4, Weidmüller | piece | 81 |  | 0
| 1.13 | Terminal block, 16mm2 E.g. WDU16, Weidmüller | piece | 9 |  | 0
| 1.14 | Copper for busbars, terminals, plastic ducts, glands, wiring, engraved nameplates, labelling material and small fittings | piece | 1 |  | 0
1.4 |  | Cable trays for the technical security system
OPOMBA: - quantities from the item 1.4 are included in the bills of quantities B1-B5 - installation shall be performed in accordance with the plan NRVB---7E/02 Načrt sistemov tehničnega varovanja
| 1. | Supply and installation of cable trays, min. height 50mm, set with covers, standard brackets for wall and ceiling mounting, branch joints, elements for raising and lowering, flexible levelling elements and other standard mounting elements, complete with mounting kit, strip galvanised: E.g. SKS, OBO BETTERMANN
| 1.1 | -tray dimensions W200 mm x H110 mm.
| 2. | Supply and installation of various steel profiles for auxiliary structures for laying cables and installation of distribution boards.
1.5 |  | Measurements, tests and other works
| 1. | Connection of power cables to UPS and distribution board of uninterruptible power supply of technical security systems, complete with fasteners and small fittings (cable glands, cable end caps, busbars, name plates, etc.). | set | 1 |  | 0
| 2. | Measurements and functional inspection of electrical installations, including records and reports for the entire system, to consist of: - loop impedance measurement, - isolation resistance measurement, - functional testing, - configuration of protective elements. | set | 1 |  | 0
[5 empty] | Total: | 0

## 2. Intruder alarm system
Contractor: | ARAO, Vrbina 17, 8270 Krško
Facility: | Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
Position |  | Description of equipment or service | Unit | Quantity | Price per unit (€) | Value (€)
2. |  | Intruder alarm system
Note: The types indicated are only intended as examples for the specification of technical characteristics and qualities. Equipment from other manufacturers of better or equivalent qualities and functionalities may also be supplied. Components supplied for the intruder alarm system must meet the requirements of Grade 2 equipment as per SIST EN 50131 or those of a higher grade. The time needed for a signal to be transmitted to the VNC in the case of alarm events or for an interruption of the transmission path or a fault in transmission to the VNC to be detected complies with the ATS 4 criterion under SIST EN 50136.
2.1 |  | Intruder alarm control unit
| 1. | Supply and installation of an intruder alarm control unit, 16 inputs expandable to 128 inputs, 6 outputs expandable to 54, with integrated PSTN telephone dialler with relevant protocols for connection to the security control centre, 12V/1.5A power supply and tamper switch. Possibility of connection of up to 16 series 500 keypads; GSM interface for message transmission. Control unit compliant with EN50131 (GRADE 3). For example: MP500/16 (80MP5L00111), Urmet | piece | 1 |  | 0
| 2. | Supply and installation of a Slovene-language module for vocal messages and remote management of control unit (via telephone). For example: SV 500N (80CT6615111), Urmet | piece | 1 |  | 0
| 3. | Supply and installation of expansion module, 8 alarm inputs + tamper input, 3 outputs (2 electric and 1 relay). For example: EP 508 (80MP7K00211), Urmet | piece | 4 |  | 0
| 4. | Supply and installation of protective plastic casing for expansion module. For example: CP/EX (80MP4J00111), Urmet | piece | 1 |  | 0
| 5. | Supply and installation of GSM module for transmission of data via the GSM/UMTS network, communicating alarm events, SMS alarm messages and vocal messages (only with vocal module). NOTE: Requires SIM card. The SIM card will be provided by the contracting authority. For example: IMG/500 (80CT5510111), Urmet | piece | 1 |  | 0
| 6. | Supply and installation of additional power supply unit with integrated power unit in plastic casing, housing for one 7Ah battery, integrated control module for battery testing and fault detection, power supply: 100Vac–260Vac, output voltage: 13.8Vdc, current: 1A, dimensions (h x w x d): 318 x 422 x 91 mm. For example: AS07/S (80PS3500211), Urmet | piece | 1 |  | 0
| 7. | Supply and installation of power supply unit with integrated power unit in metal housing, two built-in EP508 extension units, option of installing two additional expansion units, 3x programmable outputs, 2 outputs for auxiliary power units, housing for one 12V 17Ah battery, integrated control module for battery testing and fault detection, power supply: 100Vac–260Vac, output voltage: 13.8Vdc, current: 3.4 A, dimensions (h x w x d): 350 x 490 x 145 mm. For example: AS500/RPT (80PS5500111), Urmet | piece | 2 |  | 0
| 1. | Supply and installation of code keypad for management of control unit, LCD display, backlit keys, BUS connection, 2 x alarm inputs, compliant with EN50131 + voice communication (speech synthesis module). For example: KP500DV/N (80KP7200111), Urmet | piece | 1 |  | 0
2.3 |  | Web interface
| 1. | Supply and installation of an interface for the connection of the intruder alarm control unit to the local area network (LAN). Allows management of the system via any device with an internet browser (computer, smartphone, tablet, etc.). The interface is to be installed in a housing. For example: IT500WEB (80IT2710111), Urmet | piece | 1 |  | 0
2.4 |  | Intrusion detectors (IR and MW)
| 1. | Supply and installation of an antimasking dual technology (PIR and 10.5Ghz MW) intrusion detector, 12Vdc power supply, range 15m, operating temperature -10°C/+55°C, dimensions: 107x61.5x43.5mm, IR coverage: 90°, MW coverage: horizontal 90°, vertical 36°. For example: DT15AM (80IM3600113), Urmet | piece | 27 |  | 0
| 2. | Supply and installation of mounting bracket for detectors with 90° horizontal/vertical adjustment. For example: 80SP1E00113, Urmet (code applies to packs of 10) | piece | 27 |  | 0
2.5 |  | Additional intrusion detectors
| 1. | Supply and installation of brass recessed magnetic contact, anti-tamper, dimensions: 33 mm ø 8 mm, max. working distance: 10 mm, suitable for installation in aluminium and wooden windows or doors. NOTE: We recommend that recessed magnetic contacts are installed by the manufacturer of the windows or doors during manufacture of the latter. E.g.: 1033/703, Urmet | piece | 15 |  | 0
| 2. | Supply and installation of magnetic contact for lifting doors with double magnetic balancing, IP65, aluminium, max. working distance: 18 mm For example: 80MM4800213, Urmet | piece | 2 |  | 0
2.6 |  | Detection system on the perimeter fence of the secure area
| 1. | Supply and installation of control unit for perimeter detection system that can control two line controllers, Ethernet connection, RS485, internal 4Gb SD card, IP 20, DIN rail mounted. For example: PERIDECT-CUP+, Palisada Sistemi | piece | 1 |  | 0
| 2. | Supply and installation of line controller that can control up to 500 detection sensors, galvanically isolated from detection line, IP20. For example: PERIDECT-LCP+, Palisada Sistemi | piece | 2 |  | 0
| 3. | Supply and installation of detection sensor for STANDARD perimeter detection system. The sensor is addressable, with information transmitted by data cable to the evaluation unit. On supply, sensors are connected to each other at a distance of 1–5 m, depending on the contracting authority’s specification. The price includes 10 m of connection cable, PVC cable ties and screws. Protection level of detector IP 65, protection level of PVC casing IP 43. For example: PERIDECT-DSP+/S/B/26, Palisada Sistemi | piece | 420 |  | 0
| 4. | Supply and installation of detection sensor for STANDARD perimeter detection system. The sensor is addressable, with information transmitted by data cable to the evaluation unit. Protection level of detector IP 65, protection level of PVC casing IP 43. For example: PERIDECT-DSP+/S/B/00, Palisada Sistemi | piece | 5 |  | 0
| 5. | Supply and installation of standard two-channel line input for perimeter detection system. The sensor is addressable anywhere in the detection line. Protection level of detector IP 65, protection level of PVC casing IP 43. For example: PERIDECT-LIP+/S, Palisada Sistemi | piece | 8 |  | 0
| 6. | Supply and installation of standard line separator for perimeter detection system. Automatically separates the section where a technical fault (e.g. short circuit) is detected. Protection level of detector IP 65, protection level of PVC casing IP 43. For example: PERIDECT-LSP+/S, Palisada Sistemi | piece | 40 |  | 0
| 7. | Supply and installation of standard overvoltage protection module for perimeter detection system. Protection level of protection module IP 65, protection level of casing IP 43. For example: PERIDECT-LPP+/S, Palisada Sistemi | piece | 20 |  | 0
| 8. | Supply and installation of LAN input/output module, with 16-relay contacts. For example: PERIDECT-IOP+/LAN, Palisada Sistemi | piece | 1 |  | 0
| 9. | Supply and installation of PVC cable ties (pack of 100) to attach data cable to fence, approx. 10x between sensors. For example: RT-330UV, Palisada Sistemi | piece | 42 |  | 0
| 10. | Supply and installation of UR2 connectors (pack of 100). | piece | 1 |  | 0
| 11. | Supply of crimping pliers for installation of UR2 connectors. | piece | 1 |  | 0
| 12. | Supply and installation of overvoltage protection, three-phase surge arrester, installation on 35 mm DIN rail, width 18 mm. For example: BDM-48, Palisada Sistemi | piece | 2 |  | 0
| 13. | Supply and installation of cabinet for system components; dimensions W50xH70xD20mm. | piece | 4 |  | 0
2.7 |  | Sirens for intruder alarm system
| 1. | Supply and installation of HPA700M external siren, self-powered with flasher, metal casing, sound power level 110dB@1m, protection level IP 44/IK08, (requires battery) 12V 2.2Ah, operating temperature -25°C/+70°C, dimensions: 203x253x87 mm. For example: 80HP9A00211, Urmet | piece | 2 |  | 0
| 2. | Supply and installation of battery, 12V, 2Ah for fitting in external siren. For example: 1033/600, Urmet | piece | 2 |  | 0
| 3. | Supply and installation of internal siren, 12–24V, surface-mount installation, 110dB/1m, 3500–3700Hz, 145x100x42 mm. For example: HPA100 (80HP9300111), Urmet | piece | 1 |  | 0
2.8 |  | Alarm cables and UTP cables
| 1. | Supply and installation of cables, including labelling accessories, small fittings and connectors:
| 1.1 | Alarm cable 2x0.75mm2 4x0.22mm2 | m | 2750 |  | 0
| 1.2 | UTP Cat.6 cable | m | 70 |  | 0
| 1.3 | Instrumentation cable, soft core, with braiding, YSLCY-JZ 2x1mm2 | m | 200 |  | 0
| 2. | Supply and installation of PN pipes, rigid and flexible, diameter 16mm to 36mm, set including elbows, fastenings. | m | 300 |  | 0
2.9 |  | Measurements, tests and other works
| 1. | Technical support in installation of equipment. | piece | 1 |  | 0
| 2. | Connection, programming and preparation of system status displays, functional testing, preparation of a description of the as-built condition in the form of a template for the PID, submission of documentation on operation and maintenance and user training. | piece | 1 |  | 0
| 3. | Testing and verification of the system with modelled cybersecurity threats. | piece | 1 |  | 0
SUPPLY AND INSTALLATION OF EQUIPMENT IN PHASE 2 OF CONSTRUCTION OF THE REPOSITORY
2.10 |  | Intrusion detectors (IR and MW)
| 1. | Supply and installation of an antimasking dual technology (PIR and 10.5Ghz MW) intrusion detector, 12Vdc power supply, range 15m, operating temperature -10°C/+55°C, dimensions: 107x61.5x43.5mm, IR coverage: 90°, MW coverage: horizontal 90°, vertical 36°. For example: DT15AM (80IM3600113), Urmet | piece | 2 |  | 0
| 2. | Supply and installation of mounting bracket for detectors with 90° horizontal/vertical adjustment. For example: 80SP1E00113, Urmet (code applies to packs of 10) | piece | 2 |  | 0
2.11 |  | Additional intrusion detectors
| 1. | Supply and installation of brass recessed magnetic contact, anti-tamper, dimensions: 33 mm ø 8 mm, max. working distance: 10 mm, suitable for installation in aluminium and wooden windows or doors. NOTE: We recommend that recessed magnetic contacts are installed by the manufacturer of the windows or doors during manufacture of the latter. For example: 1033/703, Urmet | piece | 1 |  | 0
| 2. | Supply and installation of magnetic contact for lifting doors with double magnetic balancing, IP65, aluminium, max. working distance: 18 mm. For example: 80MM4800213, Urmet | piece | 1 |  | 0
2.12 |  | Alarm cables
| 1. | Supply and installation of cables, including labelling accessories, small fittings and connectors:
| 1.1 | Alarm cable 2x0.75mm2 4x0.22mm2 | m | 210 |  | 0
| 2. | Supply and installation of PN pipes, rigid and flexible, diameter 16mm to 36mm, set including elbows, fastenings. | m | 80 |  | 0
2.13 |  | Measurements, tests and other works
| 1. | Technical support in installation of equipment. | set | 1 |  | 0
| 2. | Connection, programming, functional testing, preparation of a description of the as-built condition in the form of a template for the PID, submission of documentation on operation and maintenance. | set | 1 |  | 0
[5 empty] | Total: | 0

## 3. Access control system
Contractor: | ARAO, Vrbina 17, 8270 Krško
Facility: | Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
Position |  | Description of equipment or service | Unit | Quantity | Price per unit (€) | Value (€)
3. |  | Access control system
Note: The types indicated are only intended as examples for the specification of technical characteristics and qualities. Equipment from other manufacturers of better or equivalent qualities and functionalities may also be supplied. Components supplied for the access control system must meet the requirements of Grade 2 equipment as per SIST EN 60839-11-1:2013.
3.1 |  | Control unit for access control system
| 1. | Supply and installation of an IPassan central unit for controlling four 2-SMART readers or receivers, expandable to max. 6 readers or receivers per control unit, 100,000 keys, 20,000 events per control unit, possibility of connection to TCP/IP network of up to 64 control units (max. 384 doors), possibility of connection to RS485 network of up to 32 control units (max. 192 doors), connection of max. 220 inputs or outputs to one control unit, lift management (max. 64 lifts) to 110 floors, DIN rail or wall mounting, power supply 12 V, dimensions: 210x145x65 mm. For example: FDI FD-125-002, Urmet | piece | 12 |  | 0
| 2. | Supply and installation of expansion module for two 2-SMART readers or receivers for IPassan controller, module increases controller capacity to 6 doors, dimensions: 200x70x26 mm. For example: FDI FD-125-010, Urmet | piece | 10 |  | 0
3.2 |  | Enclosures and power supply for installation of access control units
| 1. | Supply and installation of metal enclosure for 2 modules with 3.5A power supply unit and battery bay (battery not included), dimensions: 456x342x100 mm. For example: FDI FD-500-499, Urmet | piece | 1 |  | 0
| 2. | Supply and installation of metal enclosure for 4 modules with 7A power supply unit and battery bay (battery not included), dimensions: 456x505x100 mm. For example: 1033/601, Urmet | piece | 4 |  | 0
| 1. | Supply and installation of MULLION 2-SMART card reader 13.56 Hz for IPassan system; for surface-mount installation – internal, max. length of cables 100 m, dimensions: 78x43x17 mm. For example: FDI FD-020-081, Urmet | piece | 48 |  | 0
| 2. | Supply and installation of SINTHESI S2 2-SMART reader 13.56 Hz for IPassan system; for flush-mount installation, max. length of cables 100 m, dimensions: 85x85x16 mm. For example: FDI FD-020-176, Urmet | piece | 5 |  | 0
| 3. | Supply and installation of SINTHESI STEEL S2 2-SMART reader 13.56 Hz for IPassan system; for flush-mount installation, max. length of cables 100 m, dimensions: 85x85x16 mm. For example: FDI FD-020-132, Urmet | piece | 2 |  | 0
3.4 |  | Boxes and surrounds for readers
| 1. | Supply and installation of flush-mount box for 1 module – Sinthesi S2 reader. For example: 1145/51, Urmet | piece | 2 |  | 0
| 2. | Supply and installation of surface-mount box with roof for 1 module – Sinthesi S2 reader. For example: 1148/311, Urmet | piece | 2 |  | 0
| 3. | Supply and installation of surround for flush-mount box for Sinthesi S2. For example: 1148/61, Urmet | piece | 4 |  | 0
| 4. | Supply and installation of roof for flush-mount box for Sinthesi S2. For example: 1158/611, Urmet | piece | 2 |  | 0
3.5 |  | Cards and keys
| 1. | Supply and installation of contactless RFID key 13.56MHz, IP68, IK08, dimensions 49.5x36x7 mm, ABS VO fireproof casing. For example: FDI GB-010-010, Urmet NOTE: The number of RFID keys is specified by the investor. | piece | 50 |  | 0
| 2. | Supply and installation of contactless RFID card 13.56 MHz, dimensions: 85x54x1 mm, white PVC. For example: FDI FD-010-051, Urmet (code applies packs of 10). NOTE: The number of RFID cards is specified by the investor. | piece | 50 |  | 0
3.6 |  | Electric locks
| 1. | Supply and installation of electric lock for fence gate of main entrance to the controlled area, without unlocking in the event of fire, 12VDC/AC, 0.2A adjustable, several hours’ autonomy, with microswitch. For example: KL O&C 5U6X10, Urmet | piece | 1 |  | 0
| 2. | Supply and installation of electric lock, 24Vdc, reverse, several hours’ autonomy, with microswitch, also incorporated into the automatic fire alarm system – unlocking in the event of fire. For example: KL O&C 581F, Urmet | piece | 16 |  | 0
| 3. | Supply and installation of front plate – flat INOX for electric locks. For example: KL O&C LO3X, Urmet | piece | 16 |  | 0
| 4. | Supply and installation of electric lock – electromagnet for locking double-leaf gate/door, 300kg/2490N, 12–24Vdc / 250mA, magnet holds gate/door closed, installation on each leaf, dimensions (LxHxD) 250x48x25mm, also incorporated into the automatic fire alarm system – unlocking in the event of fire. For example: MV 1388 A, Urmet | piece | 20 |  | 0
| 5. | Supply and installation of support for electromagnet for locking double-leaf gate/door. For example: MV 300-K-STZ, Urmet | piece | 20 |  | 0
3.7 |  | Video entry system
System components by location: 1. on the entrance side of the main access to the repository plateau (perimeter fence): vandal-proof external video unit with one button and RFID card reader in surface-mount box 2. on the exit side of the main access to the repository plateau (perimeter fence): vandal-proof surface-mount box for RFID card reader 3. in the reception area of the administration and service building (security guard area): monitor with handset and desk mount; the system allows calls to be redirected to smartphones
| 1. | Supply and installation of components of video entry system at the main access to the repository plateau:
| 1.1 | - Sinthesi Steel 2voice video module. For example: 1758/83, Urmet. | piece | 1 |  | 0
| 1.2 | - Sinthesi Steel 2voice audio module For example: 1083/64, Urmet. | piece | 1 |  | 0
| 1.3 | - Sinthesi Steel one-button speech module. For example: 1158/21, Urmet. | piece | 1 |  | 0
| 1.4 | - Surface-mount box for 3 modules (without surround). For example: 1148/313, Urmet. | piece | 1 |  | 0
| 1.5 | - Sinthesi Steel surround for 3 modules with holder. For example: 1158/63, Urmet. | piece | 1 |  | 0
| 1.6 | - Surface-mount box for 1 module (without surround). For example: 1148/311, Urmet. | piece | 1 |  | 0
| 1.7 | - Sinthesi Steel surround for 1 module with holder. For example: 1158/61, Urmet. | piece | 1 |  | 0
| 1.8 | - Power supply unit for 2voice system. For example: 1083/20A, Urmet. | piece | 1 |  | 0
| 1.9 | - Additional miniature switching relay. For example: 1083/20A, Urmet. | piece | 1 |  | 0
| 1.10 | - System cable for 2voice system. For example: 1083/90, Urmet. | m | 40 |  | 0
| 2. | Supply and installation of components of video entry system in reception area:
| 2.1 | - MIRO 3.4” colour monitor with handset. For example: 1750/1, Urmet. | piece | 1 |  | 0
| 2.2 | - Desk support for 3.4” monitor. For example: 1750/92M, Urmet. | piece | 1 |  | 0
| 2.3 | - Call forwarding unit for 2voice system. For example: 1083/50, Urmet. | piece | 1 |  | 0
| 2.4 | Supply and installation of enclosure for system components; dimensions W300xH300xD210mm, RAL7035, with galvanised mounting plate, for mounting switch components on DIN rail. For example: AE system, P/N 1033.500, Rittal | piece | 1 |  | 0
3.8 |  | Power cables and FTP & UTP cables
| 1. | Supply and installation of cables, including labelling accessories, small fittings and connectors:
| 1.1 | NHXH FE 180/E90 2x1.5mm2 | m | 1280 |  | 0
| 1.2 | FTP cable | m | 2350 |  | 0
| 1.3 | UTP Cat.6 cable | m | 90 |  | 0
| 2. | Supply and installation of PN pipes, rigid and flexible, diameter 16mm to 36mm, set including elbows, fastenings. | m | 300 |  | 0
3.9 |  | Cabinet for storing physical keys – electronic key management system
Note: Cabinets for storing physical keys are not functionally connected to other components of the access control system.
| 1. | Supply and installation of cabinet for key storage in the entrance area of the ASB, number of pegs/slots/keys/steel rings: 40, electronic control of main door and individual slots, unlocking with PIN and/or access control card, operation via 7” touchscreen, stainless steel construction, connection to LAN and GSM/LTE network, 240 AC electric power supply, temporary replacement power supply in case of power outage – integrated battery, dimensions (WxHxD) 650x531x180 mm, weight 40 kg. For example: ECOS Key 40, Ecos Systems. | piece | 1 |  | 0
| 1.1 | Software for web access to cabinet, alarm module, SIM LTE card for remote access or in case of LAN failure, telephone support, automatic software upgrades. For example: ECOS Care EU package, Ecos Systems. NOTE: Supply of software is optional. | unit | 1 |  | 0
| 2. | Supply and installation of cabinet for key storage in the entrance area of the TF, number of pegs/slots/keys/steel rings: 20, electronic control of main door and individual slots, unlocking with PIN and/or access control card, operation via 7” touchscreen, stainless steel construction, connection to LAN and GSM/LTE network, 240 AC electric power supply, temporary replacement power supply in case of power outage – integrated battery, dimensions (WxHxD) 650x340x180 mm, weight 27 kg. For example: ECOS Key 20, Ecos Systems. | piece | 1 |  | 0
| 2.1 | Software for web access to cabinet, alarm module, SIM LTE card for remote access or in case of LAN failure, telephone support, automatic software upgrades. For example: ECOS Care EU package, Ecos Systems. NOTE: Supply of software is optional.
3.10 |  | Measurements, tests and other works
| 1. | Technical support in installation of equipment. | piece | 1 |  | 0
| 2. | Connection, programming and preparation of system status displays, functional testing, preparation of a description of the as-built condition in the form of a template for the PID, submission of documentation on operation and maintenance and user training. | piece | 1 |  | 0
| 3. | Testing and verification of the system with modelled cybersecurity threats. | piece | 1 |  | 0
SUPPLY AND INSTALLATION OF EQUIPMENT IN PHASE 2 OF CONSTRUCTION OF THE REPOSITORY
3.11 |  | Readers
| 1. | Supply and installation of MULLION 2-SMART card reader 13.56 Hz for IPassan system; for surface-mount installation – internal, max. length of cables 100 m, dimensions: 78x43x17 mm. For example: FDI FD-020-081, Urmet | piece | 9 |  | 0
| 2. | Supply and installation of SINTHESI S2 2-SMART reader 13.56 Hz for IPassan system; for flush-mount installation, max. length of cables 100 m, dimensions: 85x85x16 mm. For example: FDI FD-020-176, Urmet | piece | 1 |  | 0
3.12 |  | Electric locks
| 1. | Supply and installation of electric lock, 24Vdc, reverse, several hours’ autonomy, with microswitch, also incorporated into the automatic fire alarm system – unlocking in the event of fire. For example: KL O&C 581F, Urmet | piece | 5 |  | 0
| 2. | Supply and installation of front plate – flat INOX for electric locks. For example: KL O&C LO3X, Urmet | piece | 5 |  | 0
3.13 |  | Power cables and FTP cables
| 1. | Supply and installation of cables, including labelling accessories, small fittings and connectors:
| 1.1 | NHXH FE 180/E90 2x1.5mm2 | m | 170 |  | 0
| 1.2 | FTP cable | m | 340 |  | 0
| 2. | Supply and installation of PN pipes, rigid and flexible, diameter 16mm to 36mm, set including elbows, fastenings. | m | 80 |  | 0
3.14 |  | Measurements, tests and other works
| 1. | Technical support in installation of equipment. | set | 1 |  | 0
| 2. | Connection, programming, functional testing, preparation of a description of the as-built condition in the form of a template for the PID, submission of documentation on operation and maintenance. | set | 1 |  | 0
[5 empty] | Total: | 0

## 4. Video surveillance system
Contractor: | ARAO, Vrbina 17, 8270 Krško
Facility: | Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
Position |  | Description of equipment or service | Unit | Quantity | Price per unit (€) | Value (€)
4. |  | Video surveillance system
Note: The types indicated are only intended as examples for the specification of technical characteristics and qualities. Equipment from other manufacturers of better or equivalent qualities and functionalities may also be supplied. Components supplied for the video surveillance system must meet the requirements of Grade 2 equipment as per SIST EN 62676-4:2015.
4.1 |  | IP video recorders
| 1. | Supply and installation of a 32-channel IP NVR; 4 K; full HD; 1xVGA output; 1xHDMI output; 25fps real time; 32x audio inputs; 1x audio output; integrated HDD 2TB (max. 4HDD 6 TB); ONVIF; USB backup and update, mounting in rack enclosure, complete with software; 240VAC power supply, dimensions (LxHxD): 378x66x326 mm. For example: 1098/332, Urmet | set | 1 |  | 0
4.2 |  | Network switches
| 1. | Supply and installation of an 8-port PoE switch – installation in the hall above the silo; 1x optical SFP port; DIN rail mounted; 8x port 10/100Mpbs Base-T (PoE); 1x port 1000Mbps Base-X; 1x port 10/100/1000Mbps Base-T; max. 30W per port; total max. 96W; 53Vdc power supply (power supply unit supplied); dimensions: 150x100x42mm; operating temperature -30°C to 65°C. For example: PFS3110-8P-96, Urmet | piece | 1 |  | 0
| 2. | Supply and installation of a 24-port PoE switch – implemented as part of LOT 1.
| 3. | Supply and installation of a 24-port L2+ switch – implemented as part of LOT 1.
4.3 | 1. | Supply and installation of rack cabinet for recorder and network switches – implemented as part of LOT 1. The cabinet and built-in equipment must be uninstalled from the control centre for the needs of the security service during construction and installed in the administration and service building of the LILW repository.
| 1.1 | Supply and installation of a monitor socket strip – implemented as part of LOT 1.
| 2. | Supply and installation of a rack cabinet for a network switch in the technological facility; dimensions W600xH492xD600mm, RAL 7035. For example: DK system, P/N 7507.110, Rittal | piece | 1 |  | 0
| 2.1 | Supply and installation of a monitor socket strip, 19”, with 7 sockets. For example: DK system, P/N 7240.210, Rittal | piece | 1 |  | 0
| 3. | Supply and installation of enclosure for network switch in the hall above the silo; dimensions W300xH400xD210mm, RAL7035, with galvanised mounting plate, for mounting network switch on DIN rail. For example: AE system, P/N 1034.500, Rittal | piece | 1 |  | 0
| 3.1 | Supply and installation of socket for mounting on DIN rail. For example: P/N 2506.100, Rittal | piece | 1 |  | 0
| 4. | Supply and installation of cabinet for network switch, for external mounting on mast – implemented as part of LOT 1.
| 4.1 | Supply and installation of rain cover for enclosure – implemented as part of LOT 1.
| 4.2 | Supply and installation of attachment for attaching cabinet to pole – implemented as part of LOT 1.
| 4.3 | Supply and installation of socket for mounting on DIN rail – implemented as part of LOT 1.
| 4.4 | Supply and installation of heater in enclosure for outdoor installation – implemented as part of LOT 1.
| 4.5 | Supply and installation of thermostat to control heater in enclosure for outdoor installation – implemented as part of LOT 1.
4.4 |  | LCD monitors
| 1. | Supply and installation of 27.5” LCD monitor – implemented as part of LOT 1. Monitors must be uninstalled from the control centre for the needs of the security service during construction and installed in the administration and service building of the LILW repository. | set | 3 |  | 0
4.5 |  | Dome cameras with IR LED reflectors
| 1. | Supply and installation of Mini Dome STARLIGHT IP camera, 2.1Mpx; 1080p (1920x1080) HD; H.265/H.264; VDECT; 1/2.9" CMOS; recording frame rate 1–30fps@1080p, 960P, 720P; lens 2.8–12mm (31°–104°); Day&Night, ONVIF 2.6; IR range 40 m Starlight function; IP66, 1x RJ45 LAN 10/100Mbps; HTTP, TCP/IP, IPv4, UPNP, RTSP, UDP, SMTP, NTP, DHCP, DNS, PPPOE, DDNS; Multi browser; support for Urmet UVS Client via NVR; support for Mobile iUVS (iOS, Android) via NVR; power supply: 12Vcc or PoE (Power over Ethernet), consumption <7W; compatible with box 3000/102. For example: 1099/303, Urmet | piece | 11 |  | 0
4.6 |  | Compact cameras with IR LED reflectors
| 1. | Supply and installation of compact Bullet STARLIGHT IP camera, 2.1Mpx; 1080p (1920x1080) HD; H.265/H.264; VDECT; 1/2.9" CMOS; recording frame rate 1–30fps@1080p, 960P, 720P; BNC video output; lens 2.8–12mm (31°–104°); Day&Night, ONVIF 2.6; IR range 40 m Starlight function; IP66, 1x RJ45 LAN 10/100Mbps; HTTP, TCP/IP, IPv4, UPNP, RTSP, UDP, SMTP, NTP, DHCP, DNS, PPPOE, DDNS; Multi browser; support for Urmet UVS Client via NVR; support for Mobile iUVS (iOS, Android) via NVR; SD card slot; power supply: 12Vcc or PoE (Power over Ethernet), consumption <7W; compatible with box 3000/102. For example: 1099/203, Urmet | piece | 13 |  | 0
4.7 |  | Rotating cameras with IR LED reflectors
| 1. | Supply and installation of rotating EasyDome STARLIGHT IP camera – implemented as part of LOT 1.
| 2. | Supply and installation of power supply unit for Speed Dome cameras – implemented as part of LOT 1.
4.8 |  | Number plate recognition cameras
| 1. | Supply and installation of automatic number plate recognition (ANPR) camera; 8 MP; 1/1.8 CMOS; coding H.264&H.265; lens 2.7–12mm; IR illumination; degree of protection IP67, RJ45; IK10; power supply 12 V DC/24V AC/PoE+ (802.3at); ePoE. For example: IPC-HFW7842H-Z, Dahua Technology | piece | 1 |  | 0
4.9 |  | Camera accessories
| 1. | Supply and installation of surface-mount box for mounting camera. For example: 3000/102, Urmet | piece | 24 |  | 0
| 2. | Supply and installation of support for mounting cameras or boxes on posts – implemented as part of LOT 1.
| 3. | Supply and installation of support for mounting rotating cameras on posts – implemented as part of LOT 1.
| 4. | Supply and installation of power supply unit for ANPR camera, input 230 VAC, output 12 VDC, 1000 mA, for mounting in box, IP66. For example: 1092/803, Urmet | piece | 1 |  | 0
4.10 |  | Other equipment for video surveillance system
| 1. | Supply and installation of additional 4000GB hard disk for digital recorder – implemented as part of LOT 1.
| 2. | Supply and installation of IP keypad with joystick for rotating cameras – implemented as part of LOT 1.
| 3. | Video surveillance warning sticker/notice. | piece | 2 |  | 0
4.11 |  | Connectors
| 1. | Supply and installation of SFP module; TX; SM; LC. For example: PFT3960, Urmet | piece | 2 |  | 0
| 2. | Supply and installation of SFP module; RX; SM; LC. For example: PFT3970, Urmet | piece | 2 |  | 0
| 3. | Supply and installation of LC optical connector; single-mode. For example: FO-C3S, Urmet | piece | 4 |  | 0
4.12 |  | Workstation
| 1. | Supply and installation of workstation for video surveillance system including all necessary hardware and with all necessary software installed – implemented as part of LOT 1.
4.13 |  | Luminaires for illumination of perimeter fence of secure area
Note: Power cables for perimeter fence lighting are indicated in point 1.
| 1. | Supply and installation of luminaires for illumination of perimeter fence of secure area, complete with mast attachments, LED technology, mounting at a height of 9 m, min. illumination level 10 lx. For example: Luminos Ambiente LA-SL(M)-4000K(80)-95W-T2M(1.00), Nanocut | piece | 4 |  | 0
| 2. | Supply and installation of a mast h=9m with mast flange f60mm for mounting LED luminaires, powder-coated. | piece | 4 |  | 0
4.14 |  | Power cables and UTP cables
| 1. | Supply and installation of cables, including labelling accessories, small fittings and connectors:
| 1.1 | UTP Cat.6 cable PoE | m | 2000 |  | 0
| 1.2 | SM optical cable, single-core, for interior and exterior use, E.g.: 04x08 Singlemode Duct Grade UNI OS2 Leviton | m | 1300 |  | 0
| 1.3 | HDMI cable 5 m - implemented as part of LOT 1.
| 2. | Supply and installation of PN pipes, rigid and flexible, diameter 16mm to 36mm, set including elbows, fastenings. | m | 250 |  | 0
4.15 |  | Measurements, tests and other works
| 1. | Technical support in installation of equipment. | set | 1 |  | 0
| 2. | Connection, programming, functional testing, preparation of a description of the as-built condition in the form of a template for the PID, submission of documentation on operation and maintenance and user training. | set | 1 |  | 0
| 3. | Testing and verification of the system with modelled cybersecurity threats. | set | 1 |  | 0
| 4. | Technical measurements of perimeter fence lighting system to verify compliance with project-defined parameters, with creation of a measurement protocol. | set | 1 |  | 0
SUPPLY AND INSTALLATION OF EQUIPMENT IN PHASE 2 OF CONSTRUCTION OF THE REPOSITORY
4.16 |  | Compact cameras with IR LED reflectors
| 1. | Supply and installation of compact Bullet STARLIGHT IP camera, 2.1Mpx; 1080p (1920x1080) HD; H.265/H.264; VDECT; 1/2.9" CMOS; recording frame rate 1–30fps@1080p, 960P, 720P; BNC video output; lens 2.8–12mm (31°–104°); Day&Night, ONVIF 2.6; IR range 40 m Starlight function; IP66, 1x RJ45 LAN 10/100Mbps; HTTP, TCP/IP, IPv4, UPNP, RTSP, UDP, SMTP, NTP, DHCP, DNS, PPPOE, DDNS; Multi browser; support for Urmet UVS Client via NVR; support for Mobile iUVS (iOS, Android) via NVR; SD card slot; power supply: 12Vcc or PoE (Power over Ethernet), consumption <7W; compatible with box 3000/102. For example: 1099/203, Urmet | piece | 1 |  | 0
4.17 |  | Camera accessories
| 1. | Supply and installation of surface-mount box for mounting camera. For example: 3000/102, Urmet | piece | 1 |  | 0
4.18 |  | UTP cables
| 1. | Supply and installation of cables, including labelling accessories, small fittings and connectors:
| 1.1 | UTP Cat.6 cable PoE | m | 35 |  | 0
| 2. | Supply and installation of PN pipes, rigid and flexible, diameter 16mm to 36mm, set including elbows, fastenings. | m | 30 |  | 0
4.19 |  | Measurements, tests and other works
| 1. | Technical support in installation of equipment. | piece | 1 |  | 0
| 2. | Connection, programming, functional testing, preparation of a description of the as-built condition in the form of a template for the PID, submission of documentation on operation and maintenance. | piece | 1 |  | 0
[5 empty] | Total: | 0

## 5. Other works
Contractor: | ARAO, Vrbina 17, 8270 Krško
Facility: | Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
Position |  | Description of equipment or service | Unit | Quantity | Price per unit (€) | Value (€)
5. |  | Other works
| 1. | Preparation of templates for drawing up PID project. Inputting changes that occur during implementation into one copy of the PZI project. | set | 1 |  | 0
[5 empty] | Total: | 0