## Buckets delivery 2024
BUCKET NO. | TRAIN | SR(1E) | LOAD | BUCKET HEIGHT | NEMA DESC | BREAKER |  |  |  |  | STARTER |  |  |  |  | WIRE FIG. | XFR (VA) | FUSE (A) | NO. TERM BLOCKS | WIRE SIZE | OTHER/NOTES | Bucket delivery year
[6 empty] | MODEL | CURRENT INSTL. | AMPS | TRIP TYPE | SETTING | SIZE | MODEL | AUX SW (N/O) | AUX SW (N/C) | HEATER TYPE
MCC111/2CL | X | N | EPT306 | 12" | BRKR | HFD3070L | HFD3070VL | 70 | TM | [6 empty] | A |  |  |  | 2/0 |  | 2024
MCC111/2CR | X | N | SPARE BREAKER |  | BRKR | HFD3100L | HFB3100L | 100 | TM | [12 empty] | 2024
MCC111/2E | X | N | WT906MIX-001 | 12" | FVNR | HMCP050K2C |  | 50 | M | D (300 A) | 1 | A200M1CAC | 2 | 1 | FH47 | B | 100 | 3A(CTRL) 2x3A(HTR) | 12 | 6 |  | 2024
MCC111/3AL | X | N | EE106PNLG915 & 916 | 12" | BRKR | HFD3030L | HFB3030L-480 | 30 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC111/3AR | X | N | EE106PNLG913 & 914 |  | BRKR | HFD3030L | HFB3030L-480 | 30 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC111/3C | X | N | XR100XFR001(GT1 SUPPLY A) | 18" | BRKR | HFD3125L |  | 125 | TM | [6 empty] | C |  |  |  | 4/0 |  | 2024
MCC111/3E | X | N | 20302 | 18" | FVR | HMCP007C0C | HFB3110ML | 7 | M | E (49 A) | 1 | A250M1CAC | 2 | 2 | FH27 | K | 100 | 3 | 12 | 10 |  | 2024
MCC111/4A | X | N | WT114PMP-001A | 18" | FVNR | HMCP150T4C |  | 150 | M | D (900 A) | 3 | A200M3CAC | 2 | 1 | FH79 | B | 150 | 3 | 9 | 1/0 | WIRE FIG. B + 42 N/O ON 5-X2 + 42 N/C ON 4-X2 | 2024
MCC111/4B | X | N | 27001 | 18" | FVR | HMCP003A0C |  | 3 | M | A (9 A) | 1 | A250M1CAC | 2 | 2 | FH13 | K | 100 | 3 | 15 | 10 |  | 2024
MCC111/4C | X | N | 27000 | 18" | FVR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A250M1CAC | 2 | 2 | FH25 | K | 100 | 3 | 12 | 10 |  | 2024
MCC111/5A | X | N | 20525 | 18" | FVR | HMCP015E0C |  | 15 | M | C (75 A) | 1 | A250M1CAC | 2 | 2 | FH31 | K | 100 | 3 | 18 | 10 |  | 2024
MCC111/5B | X | N | 20543 | 18" | FVR | HMCP007C0C |  | 7 | M | E (49 A) | 1 | A250M1CAC | 2 | 2 | FH27 | K | 100 | 3 | 21 | 10 |  | 2024
MCC111/5C | X | N | 20579 | 18" | FVR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A250M1CAC | 2 | 2 | FH25 | K | 100 | 3 | 21 | 10 |  | 2024
MCC111/5D | X | N | VC100CPR-001 | 18" | FVNR | HMCP150T4C |  | 150 | M | E (1050 A) | 3 | A200M3CAC | 3 | 1 | FH83 | BC | 150 | 3 | 12 | 2/0 |  | 2024
MCC111/6B | X | N | CY112PMP-001 | 12" | FVNR | HMCP100R3C |  | 100 | M | F (800 A) | 2 | A200M2CAC | 2 | 2 | FH54 | B | 100 | 3A(CTRL) 2x3A(HTR) | 12 | 2 | WIRE FIG. B + 42 N/C ON 13-14 | 2024
MCC111/6C | X | N | CY110PMP-001 | 12" | FVNR | HMCP070M2C | HFB3480ML | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 1 | FH53 | B | 100 | 3 | 9 | 2 |  | 2024
MCC111/6D | X | N | LO102PMP-001 | 12" | FVNR | HMCP050K2C |  | 50 | M | F (400 A) | 2 | A200M2CAC | 2 | 1 | FH51 | B | 100 | 3 | 9 | 8 |  | 2024
MCC111/7A | X | N | WT114PMP-001 | 18" | FVNR | HMCP150T4C |  | 150 | M | D (900 A) | 3 | A200M3CAC | 2 | 1 | FH79 | B | 150 | 3 | 9 | 1/0 |  | 2024
MCC111/8AL | X | N | XR101XFR001 (T1 SUPPLY A) | 12" | BRKR | HFD3050L | HFB3050L | 50 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC111/8AR | X | N | XR101XFR002 (T2 SUPPLY A) |  | BRKR | HFD3050L | HFB3050L-480 | 50 | TM | [6 empty] | A |  |  |  | 2/0 |  | 2024
MCC111/8BL | X | N | EE106PNLG838 | 12" | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC111/8BR | X | N | EE106PNLG865 |  | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC111/8C | X | N | DR100PMP-003 | 12" | FVNR | HMCP030H1C |  | 30 | M | D (180 A) | 1 | A200M1CAC | 2 | 1 | FH43 | BI | 100 | 3A(CTRL) 2x3A(HTR) | 9 | 8 | MTR HEATER RELAY PN: AR440AR | 2024
MCC111/8D | X | N | 21179 | 18" | FVR | HMCP050K2C |  | 50 | M | F (400 A) | 2 | A250M2CAC | 2 | 2 | FH48 | K | 100 | 3 | 18 | 4 |  | 2024
MCC111/8E | X | N | 21177 | 18" | FVR | HMCP050K2C | HFB3480ML-480 | 50 | M | D (300 A) | 2 | A250M2CAC | 2 | 2 | FH48 | K | 100 | 3 | 21 | 4 |  | 2024
MCC111/9A | X | N | WT907PMP-001 | 12" | FVNR | HMCP030H1C |  | 30 | M | E (210 A) | 1 | A200M1CAC | 3 | 1 | FH46 | BC | 100 | 3 | 12 | 8 |  | 2024
MCC111/9B | X | N | VP631FAN-001 | 12" | FVNR | HMCP070M2C | HFB3480ML-480 | 70 | M | E (490 A) | 2 | A200M2CAC | 2 | 1 | FH51 | B | 100 | 3 | 9 | 8 |  | 2024
MCC111/9C | X | N | VP611PRV-011 | 12" | FVNR | HMCP070M2C | HFB3480ML-480 | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 2 | FH50 | BA | 100 | 3 | 15 | 4 |  | 2024
MCC111/9D | X | N | VP612PRV-002 | 18" | FVNR | HMCP100R3C | HMCP100R3C+ ELC3100R | 100 | M | F (800 A) | 3 | A200M3CAC | 2 | 2 | FH80 | BA | 150 | 3 | 12 | 1/0 |  | 2024
MCC111/10A | X | N | GN904DRY-002 | 18" | BRKR | HFD3015L |  | 15 | TM | [6 empty] | C |  |  |  | 8 |  | 2024
MCC111/10B | X | N | CY902PMP-001 | 12" | FVNR | HMCP050K2C |  | 50 | M | D (300 A) | 1 | A200M1CAC | 2 | 1 | FH46 | B | 100 | 3 | 12 | 8 |  | 2024
MCC111/11D | X | N | VP612PRV-003 | 18" | FVNR | HMCP100R3C | HFB31550ML-480 | 100 | M | F (800 A) | 3 | A200M3CAC | 2 | 2 | FH80 | BA | 150 | 3 | 15 | 1/0 |  | 2024
MCC111/12E | X | N | XR100XFR002 (GT2 SUPPLY A) | 18" | BRKR | JD3100C |  | 100 | TM | 5.6 (560 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
MCC112/2BL | X | N | XR101XFR003 (T1/T2 SPARE UNIT) | 12" | BRKR | HFD3015L |  | 15 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCC112/2BR | X | N | EE106PNLG979 |  | BRKR | HFD3100L |  | 100 | TM | [6 empty] | A |  |  |  | 2/0 |  | 2024
MCC112/3AL | X | N | VP641ACU-001 | 12" | BRKR | HFD3070L |  | 70 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC112/3AR | X | N | VP641HUM-001 |  | BRKR | HFD3030L |  | 30 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC112/3BL | X | N | HT101PNLG701 | 12" | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCC112/3BR | X | N | SPARE BREAKER |  | BRKR | HFD3015L | HFB3015L | 15 | TM | [6 empty] | A | [5 empty] | 2024
MCC112/3E | X | N | LS101BRDG707 | 12" | BRKR | HFD3100L |  | 100 | TM | [6 empty] | C |  |  |  | 4/0 |  | 2024
MCC112/4AL | X | N | EE106PNLG988 | 12" | BRKR | HFD3125L |  | 125 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC112/4AR | X | N | XR102XFR001A (T3 SUPPLY A) |  | BRKR | HFD3050L | HFB3480ML-480 | 50 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCC112/7AL | X | N | SX101PNL001 | 12" | BRKR | HFD3015L |  | 15 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC112/7AR | X | N | PW004PMP-03D |  | BRKR | HFD3090L |  | 90 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCC112/8FL | X | N | EP900UPS001-PRIMARY | 12" | BRKR | HFD3150L |  | 150 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC112/8FR | X | N | EP900UPS002-BYPASS |  | BRKR | HFD3150L |  | 150 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC211/1D | X | N | EE106PNLG926 | 12" | BRKR | HFD3060L | HFB3480ML-480 | 60 | TM | [6 empty] | C |  |  |  | 2 |  | 2024
MCC211/2AL | X | N | HT101PNLG702 | 12" | BRKR | HFD3015L |  | 15 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC211/2AR | X | N | EE106PNL911 (FO PUMP STATION CTRL PNL) |  |  | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC211/2B | X | N | SX913PMP-002 | 12" | FVNR | HMCP007C0C |  | 7 | M | E (49 A) | 1 | A200M1CAC | 2 | 2 | FH26 | S | 100 | 3A(CTRL) 3A(SPARE) | 9 | 10 |  | 2024
MCC211/2F | X | N | DR100PMP-004 | 12" | FVNR | HMCP030H1C |  | 30 | M | D (180 A) | 1 | A200M1CAC | 2 | 1 | FH45 | BI | 100 | 3A(CTRL) 2x3A(HTR) | 9 | 8 | MTR HEATER RELAY PN: AR440AR | 2024
MCC211/3B | X | N | VP611PRV-005 | 12" | FVNR | HMCP070M2C |  | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 2 | FH50 | BA | 100 | 3 | 12 | 4 |  | 2024
MCC211/3C | X | N | VP611PRV-006 | 12" | FVNR | HMCP070M2C |  | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 2 | FH50 | BA | 100 | 3 | 12 | 4 |  | 2024
MCC211/3D | X | N | VP611PRV-007 | 12" | FVNR | HMCP070M2C |  | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 2 | FH50 | BA | 100 | 3 | 12 | 4 |  | 2024
MCC211/3E | X | N | VP611PRV-008 | 12" | FVNR | HMCP070M2C |  | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 2 | FH50 | BA | 100 | 3 | 12 | 4 |  | 2024
MCC211/3F | X | N | VP611PRV-009 | 12" | FVNR | HMCP070M2C |  | 70 | M | D (420 A) | 2 | A200M2CAC | 2 | 2 | FH50 | BA | 100 | 3 | 12 | 4 |  | 2024
MCC211/4A | X | N | VA761PRV-001 | 12" | FVNR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A200M1CAC | 2 | 1 | FH29 | B | 100 | 1 | 9 | 10 |  | 2024
MCC211/4B | X | N | WT906MIX-002 | 12" | FVNR | HMCP050K2C |  | 50 | M | D (300 A) | 1 | A200M1CAC | 2 | 1 | FH46 | B | 100 | 3 | 12 | 6 |  | 2024
MCC211/4C | X | N | WT907PMP-002 | 12" | FVNR | HMCP030H1C |  | 30 | M | E (210 A) | 1 | A200M1CAC | 3 | 1 | FH46 | BC | 100 | 3 | 12 | 10 |  | 2024
MCC211/4D | X | N | 20303 | 18" | FVR | HMCP007C0C |  | 7 | M | E (49 A) | 1 | A250M1CAC | 2 | 2 | FH27 | K | 100 | 3 | 12 | 10 |  | 2024
MCC211/4E | X | N | HI PRESS SPLY SHUTOFF VLV GS1 | 18" | FVR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A250M1CAC | 2 | 2 | FH23 | K | 100 | 3 | 15 | 10 |  | 2024
MCC211/5AL | X | N | SPARE BREAKER | 12" | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A | [5 empty] | 2024
MCC211/5AR | X | N | GLBS GN905PNL |  |  | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC211/5B | X | N | VA761PRV-002 | 12" | FVNR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A200M1CAC | 2 | 1 | FH30 | B | 100 | 1 | 9 | 10 |  | 2024
MCC211/5C | X | N | VP631FAN-002 | 12" | FVNR | HMCP070M2C |  | 70 | M | E (490 A) | 2 | A200M2CAC | 2 | 1 | FH50 | B | 100 | 3 | 9 | 8 |  | 2024
MCC211/5D | X | N | VA761PRV-003 | 12" | FVNR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A200M1CAC | 2 | 1 | FH30 | B | 100 | 1 | 9 | 10 |  | 2024
MCC211/5E | X | N | FW105PMP002MTR-HTR | 12" | FVNR | HFD3015L |  | 15 | TM |  | 1 | A201K1CA | 1 | 1 | / | O | 100 | 3 | 6 | 10 |  | 2024
MCC211/5F | X | N | FW105PMP003MTR-HTR | 12" | FVNR | HFD3015L |  | 15 | TM |  | 1 | A201K1CA | 1 | 1 | / | O | 100 | 3 | 6 | 10 |  | 2024
MCC211/6A | X | N | 27003 | 18" | FVR | HMCP003A0C |  | 3 | M | A (9 A) | 1 | A250M1CAC | 2 | 2 | FH13 | K | 100 | 3 | 15 | 10 |  | 2024
MCC211/6B | X | N | SPILOVER SHUTOFF VLV GS3 | 18" | FVR | HMCP003A0C |  | 3 | M | C (15 A) | 1 | A250M1CAC | 2 | 2 | FH13 | K | 100 | 3 | 12 | 10 |  | 2024
MCC211/6C | X | N | 23004 | 18" | FVR | HMCP015E0C |  | 15 | M | F (120 A) | 1 | A250M1CAC | 2 | 2 | FH39 | K | 100 | 3 | 15 | 8 |  | 2024
MCC211/6D | X | N | 23007 | 18" | FVR | HMCP015E0C |  | 15 | M | F (120 A) | 1 | A250M1CAC | 2 | 2 | FH39 | K | 100 | 3 | 15 | 8 |  | 2024
MCC211/7A | X | N | 23008 | 18" | FVR | HMCP015E0C |  | 15 | M | F (120 A) | 1 | A250M1CAC | 2 | 2 | FH39 | K | 100 | 3 | 12 | 8 |  | 2024
MCC211/7B | X | N | 23011 | 18" | FVR | HMCP015E0C |  | 15 | M | F (120 A) | 1 | A250M1CAC | 2 | 2 | FH39 | K | 100 | 3 | 12 | 8 |  | 2024
MCC211/7C | X | N | 21178 | 18" | FVR | HMCP050K2C |  | 50 | M | F (400 A) | 2 | A250M2CAC | 2 | 2 | FH48 | K | 100 | 3 | 15 | 4 |  | 2024
MCC211/8C | X | N | GN900FAN-001 | 12" | FVNR | HMCP015E0C |  | 15 | M | E (105 A) | 1 | A200M1CAC | 2 | 1 | FH33 | B | 100 | 3 | 9 | 10 |  | 2024
MCC211/8D | X | N | 20524 | 18" | FVR | HMCP015E0C |  | 15 | M | C (75 A) | 1 | A250M1CAC | 2 | 2 | FH31 | K | 100 | 3 | 21 | 10 |  | 2024
MCC211/8E | X | N | 20542 | 18" | FVR | HMCP007C0C |  | 7 | M | E (49 A) | 1 | A250M1CAC | 2 | 2 | FH27 | K | 100 | 3 | 21 | 10 |  | 2024
MCC211/9BL | X | N | EP900UPS002-PRIMARY | 12" | BRKR | HFD3150L |  | 150 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC211/9BR | X | N | EP900UPS001-BYPASS |  |  | HFD3150L |  | 150 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC211/9C | X | N | SX909PNL | 12" | BRKR | HMCP007C0C |  | 7 | M | B (28 A) | [5 empty] | C |  |  |  | 8 |  | 2024
MCC211/9D | X | N | 20578 | 18" | FVR | HMCP007C0C |  | 7 | M | C (35 A) | 1 | A250M1CAC | 2 | 2 | FH25 | K | 100 | 3 | 21 | 10 |  | 2024
MCC211/9E | X | N | CY112PMP-002 | 12" | FVNR | HMCP100R3C |  | 100 | M | F (800 A) | 2 | A200M2CAC | 2 | 2 | FH54 | BA | 100 | 3A(CTRL) 2x3A(HTR) | 15 | 2 |  | 2024
MCC211/10A | X | N | IPB COOLER B (EE106PNLG768) | 18" | BRKR | JD3250C |  | 250 | TM | 10 (2500 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
MCC211/10D | X | N | VC100CPR-002 | 18" | FVNR | HMCP150T4C |  | 150 | M | E (1050 A) | 3 | A200M3CAC | 3 | 1 | FH83 | BC | 150 | 3 | 15 | 2/0 |  | 2024
MCC211/11D | X | N | WT114PMP-002A | 18" | FVNR | HMCP150T4C |  | 150 | M | D (900 A) | 3 | A200M3CACD | 2 | 1 | FH79 | * | 150 | 3 | 9 | 1/0 | * SEE ELEM. DIAGRAM (B-208) + OVERLOAD RELAY AMBIENT COMP. | 2024
MCC211/11E | X | N | LO102PMP-002 | 12" | FVNR | HMCP050K2C |  | 50 | M | F (400 A) | 2 | A200M2CAC | 2 | 1 | FH51 | B | 100 | 3 | 9 | 8 |  | 2024
MCC212/2C | X | N | EE106PNLG851 | 12" | BRKR | HFD3015L |  | 15 | TM | [6 empty] | C |  |  |  | 10 |  | 2024
MCC212/4AL | X | N | XR102XFR001A (T3 SUPPLY B) | 18" | BRKR | HFD3050L |  | 50 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCC212/4AR | X | N | LS101BRDG706 |  |  | HFD3100L |  | 100 | TM | [6 empty] | A |  |  |  | 4/0 |  | 2024
MCC212/7AL | X | N | EPT2 | 12" | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCC212/7AR | X | N | VP626ACU-001 |  |  | HFD3125L |  | 125 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC212/8AL | X | N | XR101XFR002 (T2 SUPPLY B) | 12" | BRKR | HFD3050L |  | 50 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCC212/8AR | X | N | TU099SYEG708 |  |  | HMCP003A0C | HFB3022ML | 3 | M | B (12 A) | [5 empty] | A |  |  |  | 14 |  | 2024
MCC213/1BL | X | N | LS100PNLW01 | 18" | BRKR | HFD3050L |  | 50 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCC213/1BR | X | N | CW119DORX701 |  |  | HMCP003A0C | HFB3190ML | 3 | M | C (15 A) | [5 empty] | A |  |  |  | 10 |  | 2024
MCC213/1C | X | N | PW900PMP | 12" | FVNR | HMCP050K2C |  | 50 | M | D (300 A) | 1 | A200M1CAC | 2 | 1 | FH45 | B | 100 | 3 | 15 | 6 |  | 2024
MCC213/1D | X | N | EE106PNLX946 | 18" | BRKR | JD3250C |  | 250 | TM | 10 (2500 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
MCC213/2AL | X | N | VA731HTR-006 | 12" | BRKR | HFD3015L | HFB3020 | 15 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/2AR | X | N | VA731HTR-008 |  |  | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/2B | X | N | CW105TSC-002 | 24" | FVNR | HMCP030H1C |  | 30 | M | E (210 A) | 1 | A201K1EA+ AN13P A200M1CAC | 8 | 4 | FH42 FH45 | * | 150 | 1A(CTRL) 2x3A(HTR) | 21 | 10 | * SEE ELEM. DIAGRAM (B-208) + MTR HEATER RELAY PN: AR440AR | 2024
MCC213/2C | X | N | CW105TSC-004 | 24" | FVNR | HMCP030H1C |  | 30 | M | E (210 A) | 1 | A201K1EA+ AN13P A200M1CAC | 8 | 4 | FH42 FH45 | * | 150 | 1A(CTRL) 2x3A(HTR) | 21 | 10 | * SEE ELEM. DIAGRAM (B-208) + MTR HEATER RELAY PN: AR440AR | 2024
MCC213/2D | X | N | CW901FSN-002 | 12" | FVNR | HMCP007C0C |  | 7 | M | B (28 A) | 1 | A200M1CAC | 5 | 3 | FH12 | BC | 100 | 3 | 18 | 10 | WIRE FIG. BC + 42 N/O ON 15-16 + 42 N/C ON 17-18 + 42 N/O ON 19-20 + 42 N/C ON 21-22 | 2024
MCC213/3AL | X | N | VA731HTR-010 | 12" | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/3AR | X | N | VA731HTR-012 |  |  | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/3B | X | N | 23002 | 18" | FVR | HMCP015E0C |  | 15 | M | F (120 A) | 1 | A250M1CAC | 3 | 2 | FH39 | KA | 100 | 3 | 12 | 8 |  | 2024
MCC213/3CL | X | N | EPT308 | 18" | BRKR | HFD3015L | HFB3270ML | 15 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/3CR | X | N | CW900HST-001 |  |  | HFD3015L |  | 15 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCC213/3D | X | N | CW105TSC-006 | 24" | FVNR | HMCP030H1C |  | 30 | M | E (210 A) | 1 | A201K1EA+ AN13P A200M1CAC | 8 | 4 | FH42 FH45 | * | 150 | 1A(CTRL) 2x3A(HTR) | 21 | 10 | * SEE ELEM. DIAGRAM (B-208) + MTR HEATER RELAY PN: AR440AR | 2024
MCC213/4AL | X | N | CW109PMP-002 | 12" | BRKR | HMCP030H1C | HFB3190ML | 30 | TM | D (180 A) | [5 empty] | A |  |  |  | 10 |  | 2024
MCC213/4AR | X | N | EE106PNLX871 |  |  | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/4BL | X | N | VA731HTR-002 | 12" | BRKR | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/4BR | X | N | VA731HTR-004 |  |  | HFD3020L | HFB3020L | 20 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCC213/4CL | X | N | CW105TSC001-CW105TSC003 HEATERS | 12" | BRKR | HFD3030L |  | 30 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCC213/4CR | X | N | HT101PNLX701 |  |  | HFD3025L |  | 25 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCC213/4E | X | N | LCV5600 | 12" | BRKR | HFD3015L | HFB3045ML | 15 | TM | [6 empty] | C | 200 | 2 | 3 | 10 |  | 2024
MCC213/4F | X | N | CW102PMP002MTR-HTR | 12" | FVNR | HFD3015L | HFB3045ML | 15 | TM |  | 1 | A201K1CA | 1 | 1 | / | O | 100 | 3 | 6 | 10 |  | 2024
MCCD222/2AL | X | N | FHSTFE01 | 12" | BRKR | HFD3015L | HFB3015L | 15 | TM | [6 empty] | A |  |  |  | 10 |  | 2024
MCCD222/2AR | X | N | VA431HCL001 |  |  | HFD3070L | HFD3070VL | 70 | TM | [6 empty] | A |  |  |  | 4/0 |  | 2024
MCCD222/2BL | X | N | FHSCFB01 | 12" | BRKR | HFD3015L | HFB3190ML | 15 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCCD222/2BR | X | N | MEELLD01B02 |  |  | HFD3020L |  | 20 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCCD222/2D | X | N | LS100PNLM03 | 18" | BRKR | JD3100C |  | 100 | TM | 10 (1000 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
MCCD222/2E | X | N | WPAPRS01 | 18" | FVNR | HMCP050K2C |  | 50 | M | E (350 A) | 3 | A200M3CAC | 2 | 1 | FH79 | F | 150 | 6 | 12 | 2/0 |  | 2024
MCCD222/3A | X | N | LS100PNLN06 | 18" | BRKR | JD3150C |  | 150 | TM | 10 (1500 A) | [5 empty] | C |  |  |  | 1/0 |  | 2024
MCCD222/3B | X | N | LS100PNLM04 | 18" | BRKR | JD3100C |  | 100 | TM | 10 (1000 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
MCCD222/3C | X | N | TRAPCI02 | 18" | FVNR | HMCP100R3C |  | 100 | M | F (800 A) | 3 | A200M3CAC | 3 | 2 | FH80 | BD | 150 | 6 | 12 | 1/0 |  | 2024
MCCD222/4AL | X | N | EE106PNLN943 | 12" | BRKR | HFD3040L |  | 40 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCCD222/4AR | X | N | SPARE BREAKER |  |  | HFD3020L | HFB3190ML | 20 | TM | [6 empty] | A | [5 empty] | 2024
MCCD222/4BL | X | N | FHSTTS02 | 12" | BRKR | HMCP015E0C |  | 15 | M | A (45 A) | [5 empty] | A |  |  |  | 10 |  | 2024
MCCD222/4BR | X | N | SPARE BREAKER |  |  | HFD3010L | HFB3110ML | 10 | TM | [6 empty] | A | [5 empty] | 2024
MCCD222/4C | X | N | FD901PMP-002 | 12" | FVNR | HMCP007C0C |  | 7 | M | F (56 A) | 1 | A200M1CAC | 2 | 1 | FH30 | BI | 100 | 3A(CTRL) 2x3A(HTR) | 12 | 10 | MTR HEATER RELAY PN: AR440AR | 2024
MCCD222/4D | X | N | EP900SWG003 | 12" | BRKR | HFD3070L | HFD3070VL | 70 | TM | [6 empty] | C |  |  |  | 2 |  | 2024
MCCD222/4E | X | N | 1-ALP2 | 12" | FVNR | HMCP030H1C |  | 30 | M | D (180 A) | 1 | A200M1CAC | 3 | 1 | FH39 | D | 100 | 3 | 12 | 10 |  | 2024
MCCD222/4F | X | N | CC103PMP-001 | 12" | FVNR | HMCP030H1C |  | 30 | M | E (210 A) | 1 | A200M1CAC | 2 | 1 | FH40 | B | 100 | 3 | 9 | 8 |  | 2024
MCCD222/5AL | X | N | SPARE BREAKER | 12" | BRKR | HFD3060L |  | 60 | TM | [6 empty] | A | [5 empty] | 2024
MCCD222/5AR | X | N | HD902PWR |  |  | HFD3020L | HFB3020L | 20 | TM | [6 empty] | A |  |  |  | 6 |  | 2024
MCCD222/5BL | X | N | VA202HTR-002 | 12" | BRKR | HFD3015L |  | 15 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCCD222/5BR | X | N | VA203HTR-001 |  |  | HFD3015L | HFB3015L | 15 | TM | [6 empty] | A |  |  |  | 8 |  | 2024
MCCD222/5C | X | N | SIATBI01-HTR2 | 12" | FVNR | HFD3025L | HFB3190ML | 25 | TM |  | 1 | A201K1CA | 1 | 1 | / | O | 100 | 3 | 9 | 6 |  | 2024
MCCD222/5D | X | N | FD103PMP-002 | 12" | FVNR | HMCP007C0C |  | 7 | M | F (56 A) | 1 | A200M1CAC | 2 | 1 | FH30 | BI | 100 | 3A(CTRL) 2x3A(HTR) | 12 | 10 | MTR HEATER RELAY PN: AR440AR | 2024
MCCD222/5E | X | N | SF101PMP-001 | 12" | FVNR | HMCP050K2C |  | 50 | M | D (300 A) | 1 | A200M1CAC | 2 | 1 | FH45 | B | 100 | 3 | 12 | 8 |  | 2024
MCCD222/6AL | X | N | BREVRE01A | 12" | BRKR | HFD3040L |  | 40 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCCD222/6AR | X | N | WPEVWD01A |  |  | HFD3040L |  | 40 | TM | [6 empty] | A |  |  |  | 2 |  | 2024
MCCD222/6B | X | N | GHAPGD01 | 12" | FVNR | HMCP015E0C |  | 15 | M | C (75 A) | 1 | A200M1CAC | 2 | 1 | FH33 | F | 100 | 3 | 12 | 10 |  | 2024
MCCD222/6C | X | N | WS901PMP-002 | 12" | FVNR | HMCP050K2C |  | 50 | M | D (300 A) | 2 | A200M2CAC | 2 | 2 | FH45 | BA | 100 | 3 | 12 | 4 |  | 2024
MCCD222/6D | X | N | WPAPMT02 | 18" | FVNR | HMCP050K2C |  | 50 | M | E (350 A) | 3 | A200M3CAC | 2 | 1 | FH79 | F | 150 | 6 | 12 | 1/0 |  | 2024
MCCD222/6E | X | N | GHAPCP02 | 12" | FVNR | HMCP100R3C |  | 100 | M | F (800 A) | 2 | A200M2CAC | 4 | 1 | FH57 | D | 100 | 3 | 15 | 2 | WIRE FIG. D + 42 N/O ON 15-16 | 2024
MCCD222/7AL | X | N | SPARE BREAKER | 12" | BRKR | HFD3060L |  | 60 | TM | [6 empty] | A | [5 empty] | 2024
MCCD222/7AR | X | N | RECEPTACLE |  |  | HFD3070L | HFD3070VL | 70 | TM | [6 empty] | A |  |  |  | 4 |  | 2024
MCCD222/7B | X | N | CSAPBA02 | 18" | FVNR | HMCP050K2C |  | 50 | M | E (350 A) | 3 | A200M3CAC | 2 | 1 | FH79 | F | 150 | 6 | 18 | 1/0 |  | 2024
MCCD222/7C | X | N | CF908PMP-001 | 12" | FVNR | HMCP003A0C |  | 3 | M | D (18 A) | 1 | A200M1CAC | 2 | 2 | FH19 | BA | 100 | 3 | 12 | 10 |  | 2024
MCCD222/7D | X | N | CF907TNK001 AGIT | 12" | FVNR | HMCP003A0C |  | 3 | M | C (15 A) | 1 | A200M1CAC | 2 | 2 | FH15 | BA | 100 | 3 | 12 | 10 |  | 2024
MCCD222/7E | X | N | BRAPRE02 | 18" | FVNR | HMCP050K2C |  | 50 | M | E (350 A) | 3 | A200M3CAC | 2 | 1 | FH79 | F | 150 | 3 | 18 | 1/0 |  | 2024
MCCD223/2B | X | N | LS100PNLN03 | 18" | BRKR | JD3100C |  | 100 | TM | 10 (1000 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
MCCD223/2C | X | N | VA201AHU-002 | 30" | FVNR | HMCP250J5C |  | 250 | M | E (1310 A) | 4 | A200M4CAC | 3 | 1 | FH87 | BC | 150 | 3 | 24 | 4/0 |  | 2024
MCCD223/3A | X | N | VA231FAN-002 | 30" | FVNR | HMCP250J5C |  | 250 | M | H (1640 A) | 4 | A200M4CAC | 2 | 2 | FH90 | BA | 150 | 3 | 12 | 4/0 |  | 2024
MCCD223/3B | X | N | VA241FAN-002 | 18" | FVNR | HMCP150T4C |  | 150 | M | D (900 A) | 3 | A200M3CAC | 3 | 1 | FH83 | BC | 150 | 3 | 12 | 2/0 |  | 2024
MCCD223/3C | X | N | EE106PNLM934 | 18" | FVNR | JD3100C | HFB3100L-480 | 100 | TM | 10 (1000 A) | 4 | A200M4CAC | 1 | / | / | B | 150 | 3 | 9 | 4/0 | 2x PUSH BUTTON MOUNTED AT DOOR (PN: OT2B4+OT2A) 2x IND LIGHT MOUNTED AT DOOR (PN: 125-EZC-R, 125-EZC-G) | 2024
MCCD223/4AL | X | N | HE112CRN-001 | 12" | BRKR | HFD3050L |  | 50 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCCD223/4AR | X | N | LS100PNLN01 |  |  | HFD3030L |  | 30 | TM | [6 empty] | A |  |  |  | 4/0 |  | 2024
MCCD223/4BL | X | N | LS100PNLN02 | 18" | BRKR | HFD3050L |  | 50 | TM | [6 empty] | A |  |  |  | 1/0 |  | 2024
MCCD223/4BR | X | N | LS100PNLR02 |  |  | HFD3050L |  | 50 | TM | [6 empty] | A |  |  |  | 4/0 |  | 2024
MCCD223/4C | X | N | LS100PNLM02 | 18" | BRKR | JD3150C |  | 150 | TM | 10 (1500 A) | [5 empty] | C |  |  |  | 4/0 |  | 2024
SUM
|  |  | BUCKETS TYPE BRKR = | 49
|  |  | BUCKETS TYPE FVNR = | 60
|  |  | BUCKETS TYPE FVR = | 21
130