## RECAPITULATION
Contractor: ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
A.6 | EXTERIOR ARRANGEMENTS
RECAPITULATION OF CONSTRUCTION WORK COSTS
A.6.1 | EXTERIOR ARRANGEMENTS – Phase 1 |  | Value (EUR)
1. | ORGANISATION OF CONSTRUCTION SITE AND OTHER WORKS DURING CONSTRUCTION |  | 0
2. | EARTHWORKS |  | 0
3. | MUNICIPAL WASTEWATER SEWER SYSTEM (F) |  | 0
4. | STORM WATER DRAINAGE SYSTEM (Mc) |  | 0
5. | CLEAN STORM WATER DRAINAGE SYSTEM (Ms) |  | 0
6. | INDUSTRIAL WASTEWATER DRAINAGE SYSTEM |  | 0
7. | EXTERNAL POWER LINES FOR MECHANICAL INSTALLATIONS (construction work) |  | 0
8. | EXTERNAL POWER LINES FOR ELECTRICAL INSTALLATIONS (construction works) |  | 0
9. | PHYSICAL SECURITY (within the scope of LOT 1)
10. | TRANSPORT AREAS |  | 0
11. | TRAFFIC SIGNS AND MARKINGS |  | 0
12. | INNER FENCE |  | 0
13. | MONITORING DURING CONSTRUCTION
| TOTAL |  | 0
| Unforeseen works | 5% | 0
| TOTAL Phase 1: |  | 0
A.6.2 | EXTERIOR ARRANGEMENTS – Phase 2 |  | 0
| Unforeseen works | 5% | 0
| TOTAL Phase 2: |  | 0
| EXTERIOR ARRANGEMENTS – Phases 1 and 2 |  | 0

## 1. Construction
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
A.1. | ORGANISATION OF CONSTRUCTION SITE AND OTHER WORKS DURING CONSTRUCTION
Position | Description | Unit | Quantity | Price | Value
General provisions: Accompanying works include: – construction site organisation, protection and marking, fencing and temporary structures; – organisation of occupational health and safety with all necessary studies; - ongoing surveying work; - costs of construction site connections, coordination of construction works; - insurance of contractors and facility for duration of construction works; organisation of all technical inspections and measurements; ongoing and final cleaning, continuous protection of finished elements, restoration of the environment to its original state; removal of surplus material to a municipal waste disposal facility, with record-keeping and payment of fees, internal and external transport; personnel, handling and overhead costs of contractors on site; All the above should comply with the standards and general practice applicable in Slovenia (Združenje gradbeništva Slovenije/Slovenian Construction Association) and the requirements of the design and tender documentation. The unit prices must include all construction site organisation costs in accordance with Safety Plan NRVB---7P/10 and Special Technical Conditions for Organisation of the Construction Site NRVB---6X1020.
1. | Complete construction site organisation for the entire scope of works covered by the tender and for the entire duration of construction up to the final handover of the facilities to the developer. The works cover: – the erection of temporary construction site structures; – the arrangement of temporary communication and transport routes with traffic signs and markings and connections to public roads, with all necessary documentation, permits and approvals; – the preparation of areas for the installation of temporary structures and restoration of these areas after the completion of works; – the securing of the construction site from its surroundings and from third parties (fences); – the temporary supply of water, energy and telephone services, and wastewater management; – measures to ensure occupational health and safety at the construction site; – environmental protection measures; – the management of waste generated at the construction site in accordance with regulations (removal to a regulated waste disposal site); – regular testing in accordance with the project design and regulations; – maintenance of the construction site area: mowing (mulching) in the area of the non-load-bearing embankment, humus landfill, etc., controlling of invasive plants and weeds in the area of the load-bearing embankment, etc.;
– all other activities and works necessary for the construction and completion of the works concerned in accordance with general construction practices and standards applicable in Slovenia, other than those shown under separate headings in this inventory.
1.1 | – Establishment of construction site | set | 1 |  | 0
1.2 | – Operation and maintenance of the entire construction site including the temporary access road from Vrbinska cesta to the LILW repository fence for the duration of the construction period (to be billed on a monthly basis according to the duration of site operation). | monthly | 30 |  | 0
1.3 | – Construction site clearance, clean-up and restoration to its final state in accordance with the project design documentation | set | 1 |  | 0
1.4. | – Removal of the temporary construction site road from the Vrbinska cesta junction to the LILW repository fence after the completion of works, with landscaping in accordance with the project design documentation. | set | 1 |  | 0
2. | Complete works for the provision of capacities and amenities for the contracting authority’s use in accordance with the tender documentation (Special Technical Conditions for Organisation of the Construction Site, document no. NRVB---6X1020)
2.1 | Container complex approx. 12 x 35 m (approx. 420 m2) with all interior fittings, fire extinguishers, footwear-cleaning equipment as per the tender documentation | set | 1 |  | 0
2.2 | Multifunctional devices (e.g. DEVELOP Ineo + 458) | unit | 2 |  | 0
2.3 | LCD TV screen (e.g. 4K Samsung 85 inch) | unit | 1 |  | 0
2.4 | Laptop connected to LCD TV | unit | 1 |  | 0
2.5 | Communications cabinets | unit | 2 |  | 0
2.6 | – Covered and asphalted parking areas for the contracting authority’s vehicles by the containers, 25 parking places, minimum canopy length 7 m. Approximate asphalted surface area 3,400 m2 | set | 1 |  | 0
2.7 | – Operation and maintenance of facilities for the provision of capacities and amenities for the contracting authority’s use for the duration of construction (to be billed on a monthly basis according to the duration of construction site operation) | monthly | 30 |  | 0
2.8 | – Removal of facilities for the provision of capacities and amenities for the contracting authority’s use, cleaning and restoration to original state | set | 1 |  | 0
3. | Washing of wheels of machinery before its exit from the construction site for the duration of the works in accordance with the requirements of the EIA and the tender conditions, e.g. via the installation, maintenance and removal at the end of the works of an automated mobile car wash for lorries and construction machinery of appropriate dimensions and capacity, with connections to the construction site’s LV network and water supply. | set | 1 |  | 0
4. | Complete erection of a construction site signboard up to 6 m2 in size, with supporting structure, foundations and information in accordance with regulations and the contracting authority’s requirements. Maintenance of the signboard for the duration of construction and its removal upon the completion of works. | unit | 2 |  | 0
5. | STAIRCASE FOR ACCESS TO THE SILO DURING CONSTRUCTION WORKS
Supply and erection of metal structures in the silo made of hot-dip galvanised S235JR structural steel elements. The contractor shall also include in the unit price the design, the structural assessment of the structure, the preparation of the workshop documentation and the proof of the reliability of the structure, execution class EXC 2. Design, supply and installation in accordance with the Special Technical Conditions for Organisation of the Construction Site, NRVB---6X1020 report, point 3.11.
5.1 | Preparation of PZI and workshop documentation in accordance with the Construction Act and the Rules on the detailed content of documentation and forms associated with civil construction for the entire access staircase to the silo, including anchoring in the silo floor slab and the arrangement of assembly passages to worksite areas. The structure must be capable of being fully dismantled and of providing the essential characteristics of a building for general/public use. | set | 1 |  | 0
5.2 | Manufacture, supply and erection of a hot-dip galvanised steel staircase with complete equipment, anchoring elements, handrails, walkways, prefabricated ramps for access to working areas, exit ramp from the staircase, substructure for risers and optional lift. Staircase comprising: | set | 1 |  | 0
Load-bearing structure: 140 t
Grated walkway 22/22-30/3 mm with reinforced edges: 480 m2
Treads from grated walkway 22/22-30/3 mm with reinforced and non-slip edge, size 28 x 150 cm, 290 pcs
Staircase and landing handrails, vertical bars at intervals of 10 cm and front edge 660 m.
5.3 | Dismantling of complete staircase with loading and removal to the contracting authority’s depot up to 20 km away | set | 1 |  | 0
5.4 | Removal of the temporary construction site road after the completion of works, with landscaping in accordance with the project design documentation | set | 1 |  | 0
6. | PHYSICAL AND TECHNICAL SECURITY OF THE SITE within the scope of LOT 1
CLEANING
7. | Final general cleaning of the entire construction site, facilities (TB, ASB, hall above the silo and other minor structures), equipment and exterior arrangement areas prior to the technical inspection and the handover of the facilities to the contracting authority. | set | 1 |  | 0
SURVEYING WORKS for the entire scope of LOT 2
8. | General provision for surveying work: Any surveying work ancillary to the execution of construction works, such as measuring the height of individual construction elements, restoring stable stakeout points and axes and the performance of any other surveying work not specifically listed in this inventory of works are included in the unit prices of each item or in the general operating costs of the construction site. The contractor shall be granted one stakeout for each element for all phases of the works. The contractor shall also ensure that the stakeout points are secured after stakeout. If the stakeout points are destroyed during construction, the contractor shall replace them at its own expense.
9. | Official stakeout of the repository sites that are the subject of the invitation to tender in accordance with surveying regulations Preparation of stakeout documentation with a stakeout record | set | 1 |  | 0
10. | Stakeout of the axis of the road, on flat terrain – internal roads | m | 500 |  | 0
11. | Establishment of profiles, stakeout on both sides and other ancillary works with all dimensions and measurements, – on flat terrain To be billed on a monthly basis as a percentage of the contract value of the recognised works performed | set | 1 |  | 0
12. | Securing of axis profiles, on both sides with stakes secured by a lath triangle, markings on stakes, 2 x levelling and record – on flat terrain To be billed on a monthly basis as a percentage of the contract value of the recognised works performed | set | 1 |  | 0
13. | Surveying works for stakeout and establishment of profiles for excavations and embankments, roads, etc. This item includes all surveying works for the construction of the works concerned other that those shown separately under various items and those specified in the General Provisions for Surveying Works in this inventory of works. | set | 1 |  | 0
14. | Production of surveying records of the actual as-built condition of all construction works and production of a certified as-built plan | set | 1 |  | 0
15. | Preparation of documentation for the compiling of the project documentation of completed works (PID), including all drawings, changes, etc., a list with a description of the changes and handover to the contracting authority or project design company | set | 1 |  | 0
| T O T A L ORGANISATION OF CONSTRUCTION SITE AND OTHER WORKS DURING CONSTRUCTION: |  |  |  | 0

## 2. Earthworks
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
2. | EARTHWORKS
Position | Description | Unit | Quantity | Price | Value
General provisions:
The excavation of fertile soil (humus) and the construction of the embankment up to the elevation of the substructure +154.70 m or to the elevation of the humusing is covered by the “Vrbina LILW repository no. NRVB-B052/058-2” project.
Measurements of excavations and transport shall be performed on ground in its natural state, while measurements of embankments shall be performed on inbuilt ground. Unit prices shall include all costs specified in the General Conditions for Earthworks in the tender documentation.
Tree planting and greening are included in the landscaping inventory.
LANDSCAPING IN THE AREA OF THE PLATEAU AND PARKS
1. | Landscaping of areas by spreading excavated soil (precision +-5cm) prior to placing a fertile soil layer on top Shaping of the terrain to the projected gradients with gentle rolling
a. | – Green areas between buildings | m2 | 4440 |  | 0
b. | – Remaining areas within the LILW repository perimeter fence | m2 | 38500 |  | 0
c. | – Areas along the outer perimeter path | m2 | 5710 |  | 0
2. | Loosening of compacted soil prior to filling with fertile soil (humus) The method and depth of loosening shall be determined on site depending on the compacted nature of the soil. The calculation unit is the hectare (ha).
a. | – Loosening by milling to a depth of approx. 25 cm | ha | 2.9 |  | 0
b. | – Deep loosening of the soil to a depth of 25–50 cm and milling to a depth of up to 25 cm (e.g. in the area of transport routes) | ha | 2 |  | 0
3. | Humusing of green areas between buildings to a thickness of 0.30 m by loading and delivering soil from the construction site depot over an average distance of up to 500 m, spreading and levelling (precision +-3 cm)
a. | – Green areas between buildings | m3 | 1332 |  | 0
b. | – Remaining areas within the LILW repository perimeter fence | m3 | 11550 |  | 0
c. | – Areas along the outer perimeter path | m3 | 1713 |  | 0
4. | Additional fertilisation with high-quality fertiliser of natural origin containing micro-organisms that biologically activate the soil Fertiliser of the same quality as Biogrena (manufacturer Unichem d.o.o.), use of 20 kg of fertiliser per 100 m2 (2 t/ha) per layer of a thickness of approx. 30 cm Fertiliser to be buried at shallow depth As a general rule, due to the long-term nature of the construction site depot, fertile soil from the construction site depot should be fertilised. To be measured by the fertilised area of fertile soil | ha | 4.9 |  | 0
5. | If a tree is planted at the site of an existing gravel embankment, it should be replaced with soil (e.g. mulch). The item includes the excavation of the gravel embankment, its transport to a depot in the construction site area and the construction of a new earth embankment with loading and access from the depot. The gravel material must be replaced at least 3 m from a tree to a depth of at least 0.70 m (including a humus layer of 1 m). | m3 | 125 |  | 0
LANDSCAPING OF GRASSLAND AND WOODLAND
6. | Landscaping of areas to be planted with trees and the shaping of the terrain to the projected gradients or adaptation to the existing terrain The fertile soil (topsoil) layer must be at least 30 cm thick. The calculation unit is the hectare (ha). | ha | 3.3 |  | 0
7. | Landscaping of areas for sowing (arable field areas) and the shaping of the terrain to the projected gradients or adaptation to the existing terrain. The fertile soil (topsoil) layer must be at least 30 cm thick. The calculation unit is the hectare (ha). | ha | 3.6 |  | 0
8. | Loosening of fine-graded areas of fertile soil. The method of loosening should be determined on site according to the compacted nature of the soil. The calculation unit is the hectare (ha).
a. | – Loosening by milling to a depth of approx. 25 cm | ha | 4.9 |  | 0
b. | – Deep loosening of the soil to a depth of 25–50 cm and milling to a depth of up to 25 cm (e.g. in the area of transport routes) | ha | 2 |  | 0
EXISTING HUMUS SOIL DEPOT
9. | Pedological analysis of soil at the temporary depot Analysis to be carried out in the top layer (10 cm thick) and then in 1 m layers of deposited soil at three sites. The analysis should include: soil acidity (pH), available phosphorus, potassium, magnesium and organic matter. The report should include fertilisation instructions. | unit | 4 |  | 0
10. | Sowing of black clover (Trifolium pratense) for green fertilisation on the humic soil construction site depot: 20 kg/ha (sowing to take place at the depot after removal of the top layer of living soil) | ha | 1 |  | 0
REMOVAL OF SURPLUS MATERIAL
11. | Loading and removal of surplus earth material up to Category III to a permanent disposal site to be provided by the contractor, with all disposal costs and any fees | m3 | 10000 |  | 0
| T O T A L EARTHWORKS: |  |  |  | 0

## 3. Municipal wastewater sewer s
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
3. | MUNICIPAL WASTEWATER SEWER SYSTEM (F)
Position | Description | Unit | Quantity | Price | Value
General provisions:
The inventory includes the necessary works (excavation, backfilling) up to a substructure elevation of +154.70 m, i.e. in the embankment constructed in the course of the preparatory works. All other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the lot of works for the construction of the repository plateau areas.
This inventory also includes construction works for the F1 channel in the section leading between the hall above the silo and the JF1 trench. Piping is covered by the mechanical plan.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 329 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – excavation in Category III – gravel | m3 | 1160 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 353 |  | 0
4. | Supply and installation of a sand bed (0–8 mm granulation) for the laying of sewer pipes in the projected longitudinal slope, with reinforcement Production according to the pipe manufacturer’s instructions – thickness 15 cm | m3 | 53 |  | 0
5. | Delivery and backfilling of sewer pipes with gravel sand material of (0–16 mm granulation) at a height of 30 cm above the top of the pipe, with reinforcement Production according to the pipe manufacturer’s instructions | m3 | 180 |  | 0
6. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 904 |  | 0
7. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 256 |  | 0
8. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 23 |  | 0
9. | Supply and installation of sewer system PE pipes, peripheral stiffness SN 8 kN/m2, material PE100 on prepared substrate with electrofusion jointing, pipe surface cleaning, cutting and all ancillary works, materials and transfers
a. | – PE DN 160 | m | 240 |  | 0
b. | – PE DN 250 | m | 89 |  | 0
10. | Construction of PE sewer trenches with treated bottom, constructed ditch, set of rings for cover installation and all ancillary works, concrete and mortar installation and transfer to installation site, properly concreted where necessary to prevent settlement of the trench or damage due to flotation under load
a. | – trench DN 800 at depth of up to 1 m | unit | 4 |  | 0
b. | – trench DN 800 at depth of 1–1.5 m | unit | 4 |  | 0
c. | – trench DN 800 at depth of 1.5–2 m | unit | 1 |  | 0
d. | – trench DN 800 at depth of 1–1.5 m – cascading | unit | 2 |  | 0
e. | – trench DN 1000 at depth of 1.5–2 m | unit | 1 |  | 0
f. | – trench DN 1000 at depth of 2–2.5 m | unit | 2 |  | 0
g. | – trench DN 1000 at depth of 2.5–3 m | unit | 2 |  | 0
h. | – trench DN 1000 at depth of 2–2.5 m – cascading with lateral inflow | unit | 1 |  | 0
11. | Supply and installation of cast-iron covers fi60 cm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site
a. | – Class B (125 kN) | unit | 9 |  | 0
b. | – Class D (400 kN) | unit | 8 |  | 0
12. | Construction of inspection shafts, trench inlets and other sewer installations, including bed preparation, sealing of joints, etc. | unit | 40 |  | 0
13. | Inspection of sewers with a camera and preparation of a report | m | 329 |  | 0
14. | Testing of sewers and trenches for permeability, functionality and watertightness prior to backfilling of sewer pipes, in accordance with the law and applicable regulations (SIST EN 1610) | m | 329 |  | 0
| T O T A L MUNICIPAL WASTEWATER SEWER SYSTEM (F): |  |  |  | 0

## 4. Storm water drainage system-
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
4. | STORM WATER DRAINAGE SYSTEM (Mc)
Position | Description | Unit | Quantity | Price | Value
General provisions:
The inventory includes the necessary works (excavation, backfilling) up to a substructure elevation of +154.70 m, i.e. in the embankment constructed in the course of the preparatory works. All other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the lot of works for the construction of the repository plateau areas.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 674 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III – gravel | m3 | 1186 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 533 |  | 0
4. | Supply and installation of a sand bed (0–8 mm granulation) for the laying of sewer pipes in the projected longitudinal slope, with reinforcement Production according to the pipe manufacturer’s instructions – thickness 15 cm | m3 | 80 |  | 0
5. | Delivery and backfilling of sewer pipes with gravel sand material of (0–16 mm granulation) at a height of 30 cm above the top of the pipe, with reinforcement Production according to the pipe manufacturer’s instructions | m3 | 293 |  | 0
6. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 741 |  | 0
7. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 445 |  | 0
8. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 267 |  | 0
9. | Supply and installation of C20/25 concrete as an anti-flotation casing for PE trenches Concrete encasing procedures to be carried out according to the trench manufacturer’s instructions. | m3 | 9 |  | 0
10. | Supply and installation of sewer system PE pipes, peripheral stiffness SN 8 kN/m2, material PE100 on prepared substrate with electrofusion jointing, pipe surface cleaning, cutting and all ancillary works, materials and transfers
a. | – PE DN 200 – connections to drains | m | 108 |  | 0
b. | – PE DN 200 | m | 59 |  | 0
c. | – PE DN 250 | m | 311 |  | 0
d. | – PE DN 315 | m | 129 |  | 0
e. | – PE DN 400 | m | 42 |  | 0
11. | Construction of PE sewer trenches with treated bottom, constructed ditch, set of rings for cover installation and all ancillary works, concrete and mortar installation and transfer to installation site, properly concreted where necessary to prevent settlement of the trench or damage due to flotation under load
a. | – trench DN 800 at depth of up to 1 m | unit | 4 |  | 0
b. | – trench DN 800 at depth of 1–1.5 m | unit | 11 |  | 0
c. | – trench DN 800 at depth of 1–1.5 m – with additional lateral connection | unit | 1 |  | 0
d. | – trench DN 1000 at depth of 1–1.5 m | unit | 5 |  | 0
e. | – trench DN 1000 at depth of 1.5–2 m | unit | 3 |  | 0
f. | – trench DN 1000 at depth of 1–1.5 m – with additional lateral connection | unit | 1 |  | 0
g. | – trench DN 1000 at depth of 1.5–2 m – with additional lateral connection | unit | 1 |  | 0
12. | Supply and installation of cast-iron covers fi60 cm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site
| – Class D (400 kN) | unit | 25 |  | 0
13. | Complete construction of under-curb storm drains (DN500 PE shaft) to a depth of up to 2 m with a channel cover with a bearing capacity of 125 kN suitable for PE trenches | unit | 18 |  | 0
14. | Complete construction of roadway storm drains from a DN500 PE trench to a depth of up to 2 m with a channel inlet grate with 500 mm ditch with a bearing capacity of 400kN. | unit | 10 |  | 0
15. | Construction of inspection shafts, trench inlets and other sewer installations, including bed preparation, sealing of joints, etc. for all pipe diameters | unit | 72 |  | 0
16. | Connection of fi160 drain pipes to sewer pipes of any diameter | unit | 9 |  | 0
17. | Inspection of sewers with a camera and preparation of a report | m | 674 |  | 0
18. | Testing of sewers and trenches for permeability, functionality and watertightness prior to backfilling of sewer pipes, in accordance with the law and applicable regulations (SIST EN 1610) | m | 674 |  | 0
OIL SEPARATORS The earthworks for the installation of oil separators are included under the sewer system items.
19. | Complete production of a foundation load-bearing slab and protective plate coverings for oil separators:
a. | ~ preparation of the substrate for the installation of the waterproofing membrane – fine grading of the gravel substrate (precision +-1 cm) with reinforcement to a minimum compactness of Ev2=80 MPa | m2 | 77 |  | 0
b. | – waterproofing membrane such as Gefitas PE 3/300 | m2 | 77 |  | 0
c. | – concrete C25/30, XC2, PV-I, Dmax=16 mm, protective layer 4 cm | m3 | 20 |  | 0
d. | – reinforcement of all sections and grates – B500B | kg | 2000 |  | 0
e. | – formwork for the sides of the panels (expected to be 25 cm high) | m2 | 18 |  | 0
20. | Supply and installation of a prefabricated coalescing mineral oil separator, complete with cover plate and Class B 400 kN cast-iron covers and anchoring to a concrete floor slab With internal protective coating, water filling and all ancillary works and materials Oil separators to be manufactured in accordance with SIST EN 858 The oil separators must be installed and filled in accordance with the manufacturer’s instructions. The oil separators must be suitable for installation under road surfaces.
a. | – coalescing oil separator LO2 with by-pass capacity 150l/s (e.g. OIL-TECH BP 15 or equivalent) | unit | 1 |  | 0
b. | – coalescing oil separator LO3 with by-pass capacity 80l/s (e.g. OIL-TECH BP 10 or equivalent) | unit | 1 |  | 0
| T O T A L STORM WATER DRAINAGE SYSTEM (Mc) |  |  |  | 0

## 5. Clean storm water drainage s
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
5. | CLEAN STORM WATER DRAINAGE SYSTEM (Ms)
Position | Description | Unit | Quantity | Price | Value
General provisions:
The inventory includes the necessary works (excavation, backfilling) up to a substructure elevation of +154.70 m, i.e. in the embankment constructed in the course of the preparatory works. All other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the lot of works for the construction of the repository plateau areas.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 477 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III – gravel | m3 | 1230 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 442 |  | 0
4. | Supply and installation of a sand bed (0–8 mm granulation) for the laying of sewer pipes in the projected longitudinal slope, with reinforcement Production according to the pipe manufacturer’s instructions – thickness 15 cm | m3 | 52 |  | 0
5. | Delivery and backfilling of sewer pipes with gravel sand material of (0–16 mm granulation) at a height of 30 cm above the top of the pipe, with reinforcement Production according to the pipe manufacturer’s instructions | m3 | 320 |  | 0
6. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 778 |  | 0
7. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 452 |  | 0
8. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 21 |  | 0
9. | Supply and installation of sewer system PE pipes, peripheral stiffness SN 8 kN/m2, material PE100 on prepared substrate with electrofusion jointing, pipe surface cleaning, cutting and all ancillary works, materials and transfers
a. | – PE DN 110 – connections to the sliding door foundations | m | 63 |  | 0
b. | – PE DN 160 | m | 126 |  | 0
c. | – PE DN 200 | m | 88 |  | 0
d. | – PE DN 315 | m | 103 |  | 0
e. | – PE DN 400 | m | 12 |  | 0
f. | – PE DN 630 | m | 85 |  | 0
10. | Construction of PE sewer trenches with treated bottom, constructed ditch, set of rings for cover installation and all ancillary works, concrete and mortar installation and transfer to installation site, properly concreted where necessary to prevent settlement of the trench or damage due to flotation under load
a. | – trench DN 500 at depth of to 1 m – at sliding doors | unit | 9 |  | 0
b. | – trench DN 800 at depth of up to 1 m – with additional lateral connection | unit | 1 |  | 0
c. | – trench DN 800 at depth of 1–1.5 m – with additional lateral connection | unit | 5 |  | 0
d. | – trench DN 1000 at depth of 1–1.5 m | unit | 1 |  | 0
e. | – trench DN 1000 at depth of 1–1.5 m – with additional lateral connection | unit | 1 |  | 0
f. | – trench DN 1000 at depth of 1.5–2 m | unit | 1 |  | 0
g. | – trench DN 1000 at depth of 1.5–2 m – with additional lateral connection | unit | 4 |  | 0
h. | – trench DN 1000 at depth of 1–1.5 m – with additional lateral connection | unit | 1 |  | 0
i. | – trench DN 1200 at depth of 2–2.5 m – with additional lateral connection | unit | 3 |  | 0
11. | Supply and installation of cast-iron covers fi60 cm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site
a. | – Class D (400 kN) | unit | 10 |  | 0
b. | – Class B (125 kN) | unit | 7 |  | 0
12. | Supply and installation of cast-iron covers fi50 cm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site
| – Class D (400 kN) | unit | 9 |  | 0
13. | Construction of inspection shafts, trench inlets and other sewer installations, including bed preparation, sealing of joints, etc. for all pipe diameters | unit | 64 |  | 0
14. | Testing of sewers and trenches for permeability, functionality and watertightness prior to backfilling of sewer pipes, in accordance with the law and applicable regulations (SIST EN 1610) | m | 477 |  | 0
| T O T A L CLEAN STORM WATER DRAINAGE SYSTEM (Ms) |  |  |  | 0

## 6. Industrial wastewater draina
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
6. | INDUSTRIAL WASTEWATER DRAINAGE SYSTEM (T)
Position | Description | Unit | Quantity | Price | Value
General provisions:
The inventory includes the necessary works (excavation, backfilling) up to a substructure elevation of +154.70 m, i.e. in the embankment constructed in the course of the preparatory works. All other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the lot of works for the construction of the repository plateau areas.
The supply and installation of a stainless-steel sheathed pipe (INOX DN 100, fi 200 mm) is included in the mechanical installation plan. The same applies to the leak test and all other supporting documentation.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 212 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III – gravel | m3 | 610 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 230 |  | 0
4. | Supply and installation of a sand bed (0–8 mm granulation) for the laying of sewer pipes in the projected longitudinal slope, with reinforcement Production according to the pipe manufacturer’s instructions – thickness 15 cm | m3 | 35 |  | 0
5. | Delivery and backfilling of sewer pipes with gravel sand material of (0–16 mm granulation) at a height of 30 cm above the top of the pipe, with reinforcement Production according to the pipe manufacturer’s instructions | m3 | 117 |  | 0
6. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 474 |  | 0
7. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 136 |  | 0
8. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 73 |  | 0
TRENCHES – general description Proposal for the trench construction process: – production of a floor slab; – installation of the steel lining with bottom and ditches in semi-dry concrete mortar or by fixing and then grouting with cement mortar; – connection of the lining to the pipe by welding of joints; – construction of the concrete walls of the trench; – installation of a cast-iron cover.
A technical drawing/solution of the trench/pipe connection that meets the requirements for the pipe connection is an integral part of the trench (included in the price of the trench). The end cap of the PE protective pipe is placed a few centimetres from the weld of the inox lining (the PE protective cap is incorporated into the pipe frame in the mechanical section). A circular passage opening for the PE pipe lining must be provided in the concrete lining of the trench. The size of the transition opening for the pipe must be adapted to the requirements of the sheathed pipe and the seal between the sheathed pipe and the concrete lining of the trench (as detailed in the mechanical section of the project).
9. | Complete construction of the internal lining of the bottom and walls of the trench, internal dimensions 80 x 80 cm, made from 4 mm thick stainless steel sheet, including the construction of the DN 100 half-pipe ditch Steel to AISI304L or 1.4301 quality Delivery to be made to the construction site. The price also covers the production of workshop documentation and the process of installing the lining in the trench and connection to the pipeline.
a. | – trench lining approx. 1 m deep – JT2, JT1.1 and JT1.3 (approx. 120 kg) | unit | 3 |  | 0
b. | – trench lining approx. 1.4 m deep – JT1.2 and JT1.4 (approx. 160 kg) | unit | 2 |  | 0
c. | – trench lining approx. 1.5 m deep – JT1 (approx. 170 kg) | unit | 1 |  | 0
10. | Complete installation of the metal trench lining and positioning in the projected position, taking the gradients into account Installation in fresh semi-dry cement mortar or the fixing of the lining by subsequent pouring with grouting cement mortar Installation also includes joining the lining to the pipeline by welding the joints. | unit | 6 |  | 0
11. | Complete construction of the concrete part of the 80 x 80 cm trenches from concrete C30/37-XC4-XD1-XF3, PVII, Dmax=16 mm, wall thickness 25 cm including formwork and reinforcement B500B.
a. | – trenches approx. 1 m deep – JT2, JT1.1 and JT1.3 | unit | 3 |  | 0
b. | – trenches approx. 1.4 m deep – JT1.2 and JT1.4 | unit | 2 |  | 0
c. | – trenches approx. 1.5 m deep – JT1 | unit | 1 |  | 0
12. | Supply and installation of waterproof cast-iron covers 800 x 800 mm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site Cover to the quality of e.g. a TETRA standard cover
a. | – Class D (400 kN) | unit | 5 |  | 0
b. | – Class B (125 kN) | unit | 1 |  | 0
OIL SEPARATOR and TANK
The earthworks for the installation of the oil separator and the tank are included in the sewer items.
13. | Complete production of a foundation load-bearing slab and protective plate coverings for oil separators and the tank:
a. | ~ preparation of the substrate for the installation of the waterproofing membrane – fine grading of the gravel substrate (precision +-1 cm) with reinforcement to a minimum compactness of Ev2=80 MPa | m2 | 21 |  | 0
b. | – waterproofing membrane such as Gefitas PE 3/300 | m2 | 21 |  | 0
c. | – concrete C25/30, XC2, PV-I, Dmax=16 mm, protective layer 4 cm | m3 | 5 |  | 0
d. | – reinforcement of all sections and grates – B500B | kg | 500 |  | 0
e. | – formwork for the sides of the panels (expected to be 25 cm high) | m2 | 7 |  | 0
14. | Supply and installation of a prefabricated coalescing mineral oil separator, complete with cover plate and Class B 125 kN cast-iron covers and anchoring to a concrete floor slab. With internal protective coating, water filling and all ancillary works and materials. Oil separators to be manufactured in accordance with SIST EN 858. The oil separators must be installed and filled in accordance with the manufacturer’s instructions.
– coalescing oil separator LO1 with double-walled chamber with a capacity of 15l/s (e.g. OIL-TECH 15 or equivalent) The double-walled chamber is to be fitted with an interstitial leak detector.
The scope and delivery price also includes: • stainless steel connecting elements for DN100 pipes. Steel to AISI304L or 1.4301 quality Connection by welding of joints The positions of the pipe connections must correspond to the connecting pipe. • preparation of assembly drawings for installation during construction of the facility, such as assembly sketches, assembly details, etc.;
– interstitial leak detector: 230 VAC power supply, gauge must have at least 1 x relay output (no potential SPDT contact) for the leak alarm signal and 1 x 4...20 mA continuous output signal. The gauge must have an ethernet communication interface (TCP/IP) for connection to the CNS facility. Parameter monitoring must be via a web browser, complete with all integration (software) with the CNS.
· start-up and testing – test operation comprising an inspection of installations and equipment, a review of the functioning of leakage control elements, settings and achievement of the prescribed parameters; test operation lasts 72 hours uninterrupted;
supply and assembly of stainless steel nameplates with engraved markings of the equipment schematics or in agreement with the contracting authority; performance of IQ (installation qualification) checks according to the GEP commissioning protocol and documentation of the installation qualification, including rectification of original installation defects;
| performance of OQ measurements (operation qualification) and documentation of operational measurements, including setting of parameters; recording of the as-built condition – running records of any changes made during execution, plotting and recording in the PZI project documentation; and preparation of handover documentation in print and electronic form, which must include declarations, proof of reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance. | unit | 1 |  | 0
16. | Supply and installation of a double-walled horizontal tank with a diameter of 2,000 mm, length approx. 4,170 mm, useful volume, taking into account the location of the overflow outlet, must be at least 12 m3 – for the storage of process water, with two inlet openings: a DN 500 shaft for inspection access and the insertion of a submersible pump and a DN 500 shaft for connecting the interstitial leak detector and level gauge with cast-iron Class B 125 kN covers. The positions of the pipe connections must correspond to the connecting pipe. The tank is to be fitted with an interstitial leak detector.
The tank is to be equipped with a level gauge (LI, LT) and level switch (LAH, LSH). The tank must be installed and filled in accordance with the manufacturer’s instructions.
The scope and delivery price also includes – stainless steel connecting elements for DN100 pipes, connection by welding. Steel to AISI304L or 1.4301 quality The positions of the pipe connections must correspond to the connecting pipe. • preparation of assembly drawings for installation during construction of the facility, such as assembly sketches, assembly details, etc.;
– interstitial leak detector: 230 VAC power supply, meter must have at least 1 x relay output (no potential SPDT contact) for the leak alarm signal and 1 x 4...20 mA continuous output signal. The gauge must have an ethernet communication interface (TCP/IP) for connection to the CNS facility. Parameter monitoring must be via a web browser, complete with all integration (software) with the CNS.
– level measurement: 230 VAC/DC power supply, 1 x 4...20 mA continuous output signal and at least 1 x adjustable relay output (no potential SPDT contact) for high new alarm signal. The gauge must have an RS-485 communication interface (Modbus RTU) for connection to the CNS facility. Parameter monitoring must be via a web browser, complete with all integration (software) with the CNS.
· start-up and testing – test operation comprising an inspection of installations and equipment, a review of the functioning of leakage control elements, settings and achievement of the prescribed parameters; test operation lasts 72 hours uninterrupted; supply and assembly of stainless steel nameplates with engraved markings of the equipment schematics or in agreement with the contracting authority;
performance of IQ (installation qualification) checks according to the GEP commissioning protocol and documentation of the installation qualification, including rectification of original installation defects; performance of OQ measurements (operation qualification) and documentation of operational measurements, including setting of parameters;
| recording of the as-built condition – running records of any changes made during execution, plotting and recording in the PZI project documentation; and preparation of handover documentation in print and electronic form, which must include declarations, proof of reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance. | unit | 1 |  | 0
| T O T A L INDUSTRIAL WASTEWATER DRAINAGE SYSTEM |  |  |  | 0

## 7. Water supply
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
7. | EXTERNAL POWER LINES FOR MECHANICAL INSTALLATIONS (construction work)
WATER SUPPLY SYSTEM AND HYDRANT NETWORK
Position | Description | Unit | Quantity | Price | Value
General provisions:
The inventory includes the necessary works (excavation, backfilling) up to a substructure elevation of +154.70 m, i.e. in the embankment constructed in the course of the preparatory works. All other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the lot of works for the construction of the repository plateau areas.
The inventory includes construction works for the entire external hydrant network and external water supply network up to the water gauging shaft. The water gauging shaft is included in the “Infrastructure facilities” project.
1. | Stakeout of route in accordance with the stakeout data in the project – flat terrain | m | 995 |  | 0
2. | Excavation of trenches for pipes with expansion of the excavation for hydrants and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III – gravel | m3 | 1140 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 570 |  | 0
4. | Supply and installation of a sand bed (0–8 mm granulation) for the laying of sewer pipes in the projected longitudinal slope, with reinforcement Production according to the pipe manufacturer’s instructions – thickness 15 cm | m3 | 85 |  | 0
5. | Delivery and backfilling of sewer pipes with gravel sand material of (0–16 mm granulation) at a height of 20 cm above the top of the pipe, with reinforcement Production according to the pipe manufacturer’s instructions | m3 | 220 |  | 0
6. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling The price also includes the supply and installation of the warning tape. | m3 | 1135 |  | 0
7. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 305 |  | 0
8. | Supply and installation of C20/25 concrete for hydrant sub-concreting, arch concreting, etc., including all formwork | m3 | 6 |  | 0
9. | Complete construction of the foundation for a hydrant cabinet with a provisional size of 80 x 30 x 80 cm To be manufactured according to the requirements of the cabinet installer
| – earthworks included in the pipeline items | – | 0 | 0 | 0
a. | – C30/37 concrete, XF3, fine finishing of the upper surface of the foundation by levelling | m3 | 2 |  | 0
b. | – foundation formwork | m2 | 8 |  | 0
c. | – B500B foundation reinforcement for all profiles | kg | 150 |  | 0
| T O T A L EXTERNAL POWER LINES FOR MECHANICAL INSTALLATIONS: |  |  |  | 0

## 8. Electricity
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
8. | EXTERNAL POWER LINES FOR ELECTRICAL INSTALLATIONS (construction works)
Position | Description | Unit | Quantity | Price | Value
General provisions:
This inventory covers the construction work for the cable ducts for: – electrical power cables (EJ); – telecommunications cables (TKJA); and – power lines for exterior lighting (JR).
The inventory includes the necessary works (excavation, backfilling) up to a substructure elevation of +154.70 m, i.e. in the embankment constructed in the course of the preparatory works. All other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the lot of works for the construction of the repository plateau areas.
Prices also include the installation of an earthing system (galvanised tape or copper mesh). The supply of the earthing system is included in the electrical part.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project:
a. | – electrical power distribution | m | 660 |  | 0
b. | – telecommunications | m | 430 |  | 0
c. | – exterior lighting | m | 680 |  | 0
2. | Excavation of trenches for cable ducts by widening and deepening the excavation for trenches and other sewer system structures, with removal to the edge of the excavation – Excavation in Category III – gravel | m3 | 1410 |  | 0
3. | Levelling of the bottom of the channel (precision +-3 cm) and reinforcement | m2 | 1020 |  | 0
4. | Construction of a 10 cm thick bed and encasing of the cable pipe with 0–8 mm (thickness of 10 cm) (e.g. exterior lighting cable in the green area). | m3 | 72 |  | 0
5. | Backfilling of the cable sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling The price also includes the supply and installation of the warning tape. | m3 | 793 |  | 0
6. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 617 |  | 0
7. | Supply and installation of concrete C20/25 Dmax=16 mm for the concrete bed and concrete lining of the pipes, to be installed progressively between each layer of piping, with all pipes being fully concreted | m3 | 330 |  | 0
8. | Pipe concreting formwork | m2 | 800 |  | 0
9. | Grid reinforcement Q335, quality B500B, for concreting of pipes | kg | 20300 |  | 0
10. | Supply and installation of PEHD ribbed cable ducts, smooth inside, complete with warning tape and including all ancillary parts, transfers and materials (inserts, spacers, etc.):
a. | – PEHD pipes 1 x DN 110 mm – red | m | 32 |  | 0
b. | – PEHD pipes 2 x DN 110 mm – red | m | 25 |  | 0
c. | – PEHD pipes 3 x DN 110 mm – red | m | 31 |  | 0
d. | – PEHD pipes 4 x DN 110 mm – red | m | 211 |  | 0
e. | – PEHD pipes 5 x DN 110 mm – red | m | 26 |  | 0
f. | – PEHD pipes 6 x DN 110 mm – red | m | 25 |  | 0
g. | – PEHD pipes 2 x 3 x DN 110 mm – red | m | 125 |  | 0
h. | – PEHD pipes 2 x 4 x DN 110 mm – red | m | 153 |  | 0
i. | – PEHD pipes 1 x DN 50 mm – red | m | 10 |  | 0
j. | – PEHD pipes 1 x DN 110 mm – red – for exterior lighting (JR) | m | 680 |  | 0
k. | – PEHD pipes 1 x DN 110 mm – yellow | m | 7 |  | 0
l. | – PEHD pipes 2 x DN 110 mm – yellow | m | 136 |  | 0
m. | – PEHD pipes 4 x DN 110 mm – yellow | m | 261 |  | 0
n. | – PEHD pipes 1 x DN 50 mm – yellow | m | 10 |  | 0
TRENCHES
11. | Complete construction of the concrete cable duct with cable pipe connections: – concrete C30/37-XC4-XD1-XF3, PVII, Dmax=16 mm, – bedding concrete C12/15-XC0, – reinforcement B500B, – formwork, – infiltration tunnel at the bottom of the trench made of 110 mm PEHD pipe, length 0.5 m, drainage embankment 0.125 m3 Trenches to be constructed in accordance with the PZI documentation.
a. | – Electrical power cable (EJ) trenches with clear dimensions 200 x 200 x 150 cm | unit | 3 |  | 0
b. | – Electrical power cable (EJ) trenches with clear dimensions 150 x 150 x 100 cm | unit | 12 |  | 0
c. | – Electrical power cable (EJ) trenches with clear dimensions 120 x 120 x 100 cm | unit | 2 |  | 0
d. | – telecommunications (TKJA) trenches with clear dimensions 150 x 150 x 100 cm | unit | 1 |  | 0
e. | – telecommunications (TKJA) trenches with clear dimensions 120 x 120 x 100 cm | unit | 9 |  | 0
f. | – Exterior lighting (JR) trenches with clear dimensions 80 x 80 x 90 cm | unit | 6 |  | 0
g. | – JD1 trenches with clear dimensions 80 x 80 x 90 cm | unit | 1 |  | 0
12. | Complete construction of the mast foundation with a trench and a prefabricated concrete 40/40 cm cover (JR-P) (e.g. TL-TEMELJ foundation 100 x 100 cm x H1000 manufactured by JADRANKA d.o.o.) with consolidation of the bed, e.g. with bedding concrete, connection to the cable duct and backfilling Everything to be done in accordance with the manufacturer’s instructions | unit | 28 |  | 0
COVERS
13. | Supply and installation of cast-iron covers (EN 1214 standard) on cable trenches in accordance with the cover manufacturer’s instructions:
a. | – covers 800 x 800 mm, electrical power cable (EJ) trenches, Class D (400 kN) | unit | 2 |  | 0
b. | – covers 600 x 1,250 mm, electrical power cable (EJ) trenches, Class D (400 kN) | unit | 3 |  | 0
c. | – covers 600 x 1,250 mm, electrical power cable (EJ) trenches, Class B (125 kN) | unit | 12 |  | 0
d. | – covers 600 x 600mm, telecommunications (TKJA) trenches, Class B (125 kN) | unit | 10 |  | 0
e. | – covers 800 x 800 mm, exterior lighting (JR) trenches, Class B (125 kN) | unit | 6 |  | 0
f. | – covers 800 x 800 mm, JD1 trenches, Class B (125 kN) | unit | 1 |  | 0
SEALING of cable duct penetrations in trenches adjacent to buildings
Note: sealing between cables and protective pipes is covered under the electrical installations inventory. The contractor must ensure that the chosen system is coordinated so as to ensure that elements are compatible. Trade names are given only as an example of the quality required.
General description of sealing: Double-sided wall inserts, 150mm diameter, sealed from both sides for a wall of thickness of 250mm Installation in formwork Material: wall insert: ABS with TPE 3-rib seal Connecting pipe: PVC; ABS blind cover with TPE seal Tightness: gastight and watertight to 2.5 bar – TYPE: e.g. HSI 150-1x4-K2/200 Hauff Technik or equivalent
System covers with cold-shrink sleeve for connecting ribbed or smooth electricity cable ducts of diameter 110 mm to an HSI 150-K wall insert – Material: system cover: polycarbonate; clamping nut: PC/PBT blend; cold-shrink sleeve: EPDM – Tightness: gastight and watertight to 0.5 bar – TYPE: e.g. Hauff Technik HSI 150-D110-KS or equivalent
14. | Electrical power cable trench (EJ-1)
| Double-sided wall insert: – double-sided wall insert of diameter 150 mm sealed from both sides for wall thickness 250 mm – frame dimensions: 220 x 220 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 1 |  | 0
15. | Electrical power cable trench (EJ-2)
| Double-sided wall insert: – pack of 2 x 6 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 2; rows in width: 6 – frame dimensions: 1,270 x 430 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 12 |  | 0
16. | Electrical power cable trench (EJ-5)
| Double-sided wall insert: – pack of 6 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 1; rows in width: 6 – frame dimensions: 1,270 x 220 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 6 |  | 0
17. | Electrical power cable trench (EJ-8)
| Double-sided wall insert: – pack of 2 x 3 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 2; rows in width: 3 – frame dimensions: 640 x 430 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 6 |  | 0
18. | Electrical power cable trench (EJ-10)
| Double-sided wall insert: – pack of 5 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 1; rows in width: 5 – frame dimensions: 1,060 x 220 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 5 |  | 0
19. | Telecommunications trench (TKJA-3)
| Double-sided wall insert: – pack of 4 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 1; rows in width: 4 – frame dimensions: 850 x 220 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 4 |  | 0
20. | Telecommunications trench (TKJA-5)
| Double-sided wall insert: – pack of 4 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 1; rows in width: 4 – frame dimensions: 850 x 220 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 4 |  | 0
21. | Telecommunications trench (TKJA-8)
| Double-sided wall insert: – pack of 2 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 1; rows in width: 2 – frame dimensions: 430 x 220 mm; centre distance: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 2 |  | 0
22. | Jašek TKJA-9
| Double-sided wall insert: – pack of 3 double-sided wall inserts of diameter 150 mm sealed from both sides for wall thickness 250 mm – rows in height: 1; rows in width: 3 – frame dimensions: 640 x 220 mm; distance between axes: 210 mm | unit | 1 |  | 0
| System cover with seal | unit | 3 |  | 0
23. | Complete construction of the foundations of the street lamps 70 x 70 x 120 cm in size (for exterior lighting/JR trenches): – excavation, backfilling behind the foundations and the removal of surplus material are included under the cable duct items ~ bedding concrete C12/15 -X0, 10 cm thick, including formwork ~ concrete foundation; concrete C20/35, XC2, CI.0.2, Dmax=16mm, IFTR 100 under SIST EN 206-1 and SIST 1026, SIST EN 1992-1-1, protective layer 4 cm, performance class 2 under SIST EN 13670 and NAD, tolerance class 1 under SIST EN 13670 and NAD, treatment of visible formwork surfaces under SIST EN 13670 and NAD basic VB 2 ~ supply and installation of PE-HD pipe fi 80 mm – installation in concrete – reinforcement B500B (50 kg/pc) ~ installation of anchors and templates for lamps Anchors and templates should be sourced and supplied by the streetlight supplier, ~ point foundation formwork (formwork, formwork removal and cleaning) | unit | 6 |  | 0
24. | Excavation of a trench for earthing straps and backfilling after the strap has been laid The supply and installation of the earthing strap is covered under the electrical part. Ditch 40 cm wide and projected to be 80 cm deep | m | 1050 |  | 0
| T O T A L EXTERNAL POWER LINES FOR ELECTRICAL INSTALLATIONS (construction works): |  |  |  | 0

## 10. Transport areas
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
10. | TRANSPORT AREAS
Position | Description | Unit | Quantity | Price | Value
General provisions:
The starting point for the implementation of exterior arrangements is the height of the embankment, which has been built up to a height of 154.70 metres above sea level as part of the preparatory works.
All embankment works are invoiced according to the volume of earth in as-built state. The calculation of quantities is based on profiles taken before and after backfilling. For the purpose of billing for the works, the costs of the surveying works are included in the price of the embankment works.
GRAVEL BUFFER
1. | Preparation of the base for the gravel buffer by levelling to +-3 cm and consolidation to a minimum compaction of Ev2=80 MN/m2 | m2 | 8600 |  | 0
2. | Supply and mechanical installation of 0/32 mm buffer material, a mixture of crushed stone granules, together with compaction and levelling of the subgrade +- 1 cm (calculated as per the compacted state)
a. | – gravel buffer of a minimum thickness of 40 cm – Road 1, consolidation to a minimum of Ev2 = 120 MN/m2. | m3 | 2650 |  | 0
b. | – gravel buffer of a minimum thickness of 40 cm – Road 2, consolidation to a minimum of Ev2 = 80 MN/m2. | m3 | 960 |  | 0
c. | – gravel buffer of a minimum thickness of 30 cm – footpaths, pavements, consolidation to a minimum of Ev2 = 80 MN/m2. | m3 | 185 |  | 0
d. | – gravel buffer of a minimum thickness of 25 cm – concrete floor, consolidation to a minimum of Ev2 = 80 MN/m2. | m3 | 232.5 |  | 0
e. | – gravel buffer of a thickness of approx. 55 cm – backfill at buildings under gravel to a minimum of Ev2 = 60 MN/m2. | m3 | 190 |  | 0
ASPHALT WORKS
3. | Spraying of gravel subgrade with bitumen for the asphalt layer to ensure better bonding | m2 | 8085 |  | 0
4. | Supply and mechanical laying of a load-bearing layer of bituminised mix on a prepared buffer base of quality AC 32 base PmB 25/55-65 A2, 10 cm thick – Road 1 | m2 | 5810 |  | 0
5. | Supply and laying of a wear-resistant barrier of bituminised mix AC surf 11 PmB 45/80-65 A2, 4 cm thick – Road 1 | m2 | 5810 |  | 0
6. | Supply and mechanical laying of a load-bearing layer of bituminised mix on a prepared buffer base of quality AC 16 base B 70/100 A4, 5 cm thick – Road 2 | m2 | 2040 |  | 0
7. | Supply and laying of a wear-resistant barrier of bituminised mix AC surf 8 B 70/100 A4, 3 cm thick – Road 2 | m2 | 2040 |  | 0
8. | Supply and laying of a wear-resistant barrier of bituminised mix AC surf 8 B 70/100 A5, 4 cm thick – pavements | m2 | 235 |  | 0
KERBS
9. | Supply, spread and installation of concrete kerbs in a C12/15 concrete base with cement mortar grouting of the joints, together with earthworks and all ancillary works and transfers Deepened and raised kerbs
a. | – dimensions 15/25/100 cm | m | 980 |  | 0
b. | – dimensions 15/25/100 cm – curve | m | 130 |  | 0
b. | – dimensions 15/25/100 cm – kerb inlets | unit | 18 |  | 0
c. | – dimensions 8/20/100 cm | m | 180 |  | 0
d. | – dimensions 8/20/100 cm – curve | m | 30 |  | 0
e. | – dimensions 8/20/100 cm – adjacent to the TB and ASB | m | 260 |  | 0
d. | – dimensions 8/20/100 cm – kerb inlets | unit | 1 |  | 0
GRAVEL ADJACENT TO BUILDINGS
10. | Spreading of gravel (32 mm granulation) to a thickness of 10cm adjacent to the TB and ASB | m2 | 185 |  | 0
CONCRETE FLOORS
11. | The external reinforced concrete floor, 25 cm thick, is made of reinforced concrete of specification C30/37 XC4/XF4/XD2 Dmax 16 mm (OPZT S25). Polypropylene fibres, 10–12 mm in length (0.91 kg/m3), are added to the concrete mix. The concrete mix must use a quarried stone aggregate that is grey in colour. After pouring and compaction, the surface of the concrete is manually processed (trowelled), with all the necessary inclines being executed. Cutting of virtual dilatations is done according to the architectural or reinforcement plan of dilatations. The reinforcement is placed in each field separately.
After suitable curing, the concrete surface is machine processed, first by coarse grinding approximately 4 mm deep, and then by bush-hammering. After grinding, all larger holes in the concrete are filled with a suitable mortar (freeze-resistant XF4), which must be of a suitable colour. Only after filling is the concrete bush-hammered. Before execution, a test field of at least 1 m2 in area must be produced using the same materials and the chosen treatment process. The test field and the appearance of the surface after treatment are subject to the architect’s approval. The test field is repeated as necessary until the right appearance has been achieved and approval has been given by the architect.
a. | ~ preparation of the substrate for the installation of the waterproofing membrane – fine grading of the gravel substrate (precision +-1 cm) with reinforcement to a minimum compactness of Ev2=80 MPa | m2 | 930 |  | 0
b. | ~ waterproofing membrane such as Gefitas PE 3/300 | m2 | 930 |  | 0
c. | ~ concrete C30/37 XC4/XF4/XD2 Dmax 16 mm with microfibres | m3 | 233 |  | 0
d. | ~ bush-hammering | m2 | 930 |  | 0
e. | ~ protection of the bush-hammered surface with a coating such as Pieri Early Protect VBA immediately after surface treatment is completed | m2 | 930 |  | 0
f. | ~ test field size 1 m2 | set | 1 |  | 0
12. | Concrete C30/37 XC4/XF4/XD2 Dmax 16 mm of strip foundation under the slab | m3 | 5 |  | 0
13. | C12/15 bedding concrete under strip foundations, including any formwork | m3 | 2 |  | 0
14. | Complete construction of the dowel dilatation with installation of plastic pipes fi 32 mm for dowels, approx. 5 pcs/m, with expanded polyethylene filler, 20 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edges at an angle of 45° and to a width of 1 cm To be carried out in accordance with the reinforcement drawings. | m | 17 |  | 0
15. | Complete execution of cut grooves: • on the day after the reinforced concrete floor slab is concreted, a groove 3 mm wide and to a depth of 1/3 of the thickness of the slab must be cut • the groove line should be recut (8 mm wide, 40 mm deep) just before the pavement is put into service • the groove should be filled with a strip of polyethylene foam as a depth limiter and as a base for the sealant (e.g. Geocel PRO 592). Installation according to the instructions of the selected manufacturer of the sealing materials Grinding of the upper edges at an angle of 45° and to a width of 1 cm | m | 178 |  | 0
16. | Complete dilatation of the contact of the concrete slabs with the installation of expanded polyethylene filler, 10 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edges at an angle of 45° and to a width of 1 cm | m | 106 |  | 0
17. | Complete implementation of a gap along the curb, to be filled with expanded polyethylene filler, 10 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edge of the concrete slab, width 1 cm, 45° angle | m | 104 |  | 0
18. | Complete implementation of dilatation along the building, to be filled with expanded polyethylene filler, 10 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edge of the concrete slab, width 1 cm, 45° angle | m | 60 |  | 0
19. | Supply and installation of a 70/30/4 mm stainless steel angle iron, with anchors at 50 cm intervals and its fixing into the formwork prior to concreting | m | 233 |  | 0
20. | Supply, machining and manual assembly of concrete steel reinforcement of various profiles and B500B reinforcement grids | kg | 33000 |  | 0
21. | Formwork of floor slab edges; formwork, formwork removal and cleaning:
a. | – formwork 25 cm high – flat part | m2 | 90 |  | 0
b. | – formwork 25 cm high – curved part (R = 7.5 m) | m2 | 4 |  | 0
22. | Strip foundation formwork under the slab in the area of the fence | m2 | 21 |  | 0
EXTERNAL AND INTERNAL PERIPHERAL SERVICE ROAD is within the scope of the works in LOT 1.
FLAGPOLES
23. | Complete construction of flagpole foundations, size: 70 x 70 x 120 cm: – excavation, backfilling behind the foundations and the removal of surplus material, ~ bedding concrete C12/15 -X0, 10 cm thick, including formwork ~ concrete foundation; concrete C30/37, XF3, CI.0.2, Dmax=16mm, IFTR 100 under SIST EN 206-1 and SIST 1026, SIST EN 1992-1-1, protective layer 4 cm, performance class 2 under SIST EN 13670 and NAD, tolerance class 1 under SIST EN 13670 and NAD, treatment of visible formwork surfaces under SIST EN 13670 and NAD basic VB 2 – reinforcement B500B (50 kg/pc) – point foundation formwork (formwork, formwork removal and cleaning). – installation of anchors for the pole in the foundation using a jig with fixing in the formwork before concreting (without supply of anchors). | unit | 4 |  | 0
24. | Supply and installation of flagpoles on pre-installed anchors in reinforced concrete foundations and preparation for grounding of the poles. The actual implementation of the grounding is not part of this inventory. ~ height of poles: 7.00 m ~ diameter of pipe: 80 mm ~ rings for fastening the flag on the long side (on the pole): 6 pcs ~ transverse flag support bar: 1.00 m ~ eyelet for transverse bar: 1 item ~ material: powder-coated aluminium ~ colour: as chosen by the contracting authority ~ functionality: a tilt and turn mechanism allows the flag to turn a full circle (360°) downwind, lowering of the flag with a complete mechanism, automatic raising of the flag – steel cable and weight inside the pole ~ flag dimensions and fastening: for 100 x 300 cm flags, the shorter side is fastened horizontally on the pole and the longer side is fastened with rings. ~ flag types: as chosen by the contracting authority ~ installation: screwing of the pole into the anchor previously embedded in concrete Anchors for installation in the reinforced concrete foundation must be supplied by the post supplier. | unit | 4 |  | 0
| T O T A L TRANSPORT AREAS: |  |  |  | 0

## 11. Traffic signs and markings
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
11. | TRAFFIC SIGNS AND MARKINGS
Position | Description | Unit | Quantity | Price | Value
1. | Construction of a foundation for traffic signs, concrete C 12/15, depth 80 cm deep, diameter 40 cm | unit | 11 |  | 0
2. | Supply and installation of a traffic sign post made of hot-dip galvanised tubular steel
a. | – fi 64 mm, length 3,500 mm | unit | 10 |  | 0
b. | – fi 64 mm, length 4,000 mm | unit | 1 |  | 0
3. | Supply and fixing of a round traffic sign, aluminium sheet base
a. | 2102, octagonal STOP sign | unit | 5 |  | 0
b. | 2232-5; fi 60 cm, RA2 (speed limit 10 km/h) | unit | 1 |  | 0
c. | 2417; 40 x 40 cm; RA2 (emergency access route) | unit | 5 |  | 0
d. | 4803; supplementary board 40 cm; RA2 (access route for firefighting vehicles) | unit | 5 |  | 0
e. | – standard assembly point noticeboard | unit | 1 |  | 0
4. | Production of thin-film marking with single-component white paint, thickness of dry matter layer 300 microns
a. | line 5111 (solid dividing line), line width 15 cm | m | 25 |  | 0
b. | line 5121 (1-1-1), broken dividing line, w=15 cm | m | 175 |  | 0
c. | line 5121 (3-3-3), broken dividing line, w=15 cm | m | 410 |  | 0
d. | line 5112, solid border line along the HALL, w=15 cm | m | 153 |  | 0
e. | line 5211, solid wide transversal line, w=50 cm | m | 17 |  | 0
f. | line 5122, solid border line, width 15 cm, w=10 cm | m | 50 |  | 0
g. | line 5231, pedestrian crossing | m2 | 100 |  | 0
h. | line 5321, chevron | m2 | 15 |  | 0
5. | Production of thin-film marking with single-component yellow paint, thickness of dry matter layer 300 microns
a. | – 5340 (emergency access area) – line w=10 cm | m | 136 |  | 0
b. | – 5508 – sign “EMERGENCY ACCESS AREA” | unit | 8 |  | 0
6. | Production of marking with symbols and single-component white paint, thickness of dry matter layer 300 microns
a. | 5501 STOP | unit | 5 |  | 0
b. | symbol 5234 pedestrian pathway | unit | 21 |  | 0
7. | Production of kerb markings with ground marking tape, red-white marking, anti-slip, 75 mm wide, suitable for outdoor use, self-adhesive | m | 25 |  | 0
| T O T A L TRAFFIC SIGNS AND MARKINGS: |  |  |  | 0

## 12. Inner fence
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
12. | INNER FENCE
Position | Description | Unit | Quantity | Price | Value
INNER FENCE
General description of the fence: The fence must be fixed to the posts without screws and must not be easy to dismantle (higher level of security). Surface protection of fence elements: Zn+Epoxy+Polyester Pillars: quantity Zn-275g/mm2; polyester thickness min. 100µm Panels: Zn content min. 70g/mm2; polyester thickness min. 100µm The fencing is to be installed in the bank in cascade form (cascades every 10 cm).
The outer fence is within the scope of LOT 1.
INNER FENCE
1. | Complete supply and installation of inner panel-type fencing: – 2,030 mm high panels with vertical steel wires fi 5 mm and 2 x 6 mm horizontal wires Grid window size max. 50 x 200 mm – pillars: resistance of moment pillars W > 6.5 cm3; perpendicular to the direction of the fence Minimum pillar wall thickness 2.9 mm; cross-section 60 x 86 mm; metal pillar caps in the same colour as the pillars, fixed to the pillars before surface treatment – concrete foundations fi 30/60 cm – concrete slats 25 x 5 cm, standard length 245 cm The slats must be made of freeze-resistant concrete (min. C30/37). All metal parts of the fence should be made of steel, hot-dip galvanised and epoxy- and polyester-coated in RAL 7006 (light grey). The fence is earthed. Fence such as Palisade Bastifor N | m | 480 |  | 0
| T O T A L INNER FENCE: |  |  |  | 0

## 13. Monitoring
Developer: ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
13. | MONITORING DURING CONSTRUCTION
Monitoring during construction of LILW that comes under LOT 2
Position | Description | Unit | Quantity | Price | Value
General provisions:
The contractor shall submit all monitoring reports (written procedures) to the contracting authority in electronic form for review and approval. The contractor shall deliver 6 copies of final, approved reports to the contracting authority in printed and digital form (e.g. CD or other agreed format). Monitoring shall be done in accordance with approved written procedures/reports.
GEODETSKA OPAZOVANJA V ČASU GRADNJE
Reference documents:
Document no.: NRVB---7L0001 - Projekt vertikalne in horizontalne geodetske mreže za potrebe opazovanja premikov objektov Odlagališča NSRAO
Document no.: NRVB---7L0002 - Program geodetskih opazovanj premikov objektov Odlagališča NSRAO
1. | Establishment of horizontal and height reference geodetic network for the purposes of determination of horizontal and vertical deformations and movements of structures and plateau of the repository. Required accuracy of determination for determination of movements of control points is ± 1 mm (error ellipse).
1.1 | - elaboration of horizontal and height reference network documentation | set | 1 |  | 0
1.2 | - stabilisation of reference and control points in accordance with the approved documentation | set | 1 |  | 0
1.3 | - elaboration of a written procedure fpr the purposes of determination of horizontal and vertical deformations and movements (geodetic datum, type, methods and schedule of measurements, equipment, resources, observations analysis, detection of movements, presentation). Input data are detailed design documentation and other documentatios for construction. | set | 1 |  | 0
2. | Complete installation of reference and control points in/on structures in accordance with instructions in the detailed design documentation (requirements of a structural engineer). Control points shall be made of brass or stainless steel. Price includes delivery of material and installation into a building structure. | pcs | 45 |  | 0
3. | Complete construction of reference points on the embankment plateau in accordance with the detailed design documentation (layout, type of realisation). | pcs | 7 |  | 0
4. | Implementation of zero measurement in accordance with the monitoring project and an elaboration report. | set | 1 |  | 0
5. | Implementation of regular periodic and extraordinary observations during construction in accordance with design documentation. Measurements of rock movements during excavation of the construction pit and movements of civil structures during construction (silo, control pool, technological facility, plateau). To be billed monthly in an amount proportional to the percentage of completed structures that are being measured. | set | 1 |  | 0
6. | Elaboration of the final report of geodetic monitoring during construction report and delivery to client in 6 copies and a digital form on a CD. | set | 1 |  | 0
TECHNICAL MONITORING
1. | Technical monitoring of silo facility
Reference documents:
7/1 Primary substructure
7/2 Protection of construction pit against hydraulic collapse
7/3 Geotechnical monitoring plan
| Complete implementation of technical monitoring of the silo facility with elaboration of a written procedure in accordance with the monitoring guidelines and criteria set out in the tender documents and the PZI project, including the preparation of reports. Monitoring shall cover: a. the method and effectiveness of implementation of pumping of groundwater in relief wells (after the excavation and construction phases); b. the permeability of the primary liner of the silo (joints, cracks); c. the erosion of rock in relation to the permeability of the primary liner; d. the permeability of the secondary liner of the silo (joints, cracks). To be billed monthly in an amount proportional to the percentage of work completed for the silo. | set | 1 |  | 0
2. | Technical monitoring of facilities
Reference documents: Programme of technical monitoring during the construction phase, detailed report No. NRVB---7P/01, June 2021
| Implementation of technical monitoring in accordance with Technical Monitoring Programme NRVB---7P/01 (the Programme). The unit price for implementation of technical monitoring must take into account the full scope of monitoring and the planned periodicity as per the Programme, the preparation of a written procedure covering the implementation of inspections in all segments throughout construction, with the periodicity envisaged in Table 2-1 of the Programme, and the elaboration of intermediate reports and a final report with analysis of results with regard to defined project baselines. Service to be billed in accordance with a submitted report that has been approved by a representative of the contracting authority, on a percentage basis corresponding to the envisaged scope of monitoring during construction. | set | 1 |  | 0
3. | Geological and geotechnical monitoring of construction
GENERAL
Geological and geotechnical monitoring shall be carried out in accordance with the instruction set out in the General Technical Requirements, Chapter A – Earthworks and Geotechnical Works, point 1.4. Geological and geotechnical monitoring of construction. Unit prices must include all costs necessary for the contents of a uniform implementation of all works laid down in the General Technical Requirements.
3.1 | Elaboration and coordination of a detailed report on the implementation of geological and geotechnical monitoring of construction in accordance with General Technical Requirements, Chapter A – Earthworks and Geotechnical Works, point 1.4. Geological and geotechnical monitoring of construction and 7/3 Geotechnical monitoring plan. | set | 1 |  | 0
3.2 | Ongoing monitoring of all earthworks and geotechnical works, keeping of daily records, mapping, photo-documentation, soil sampling in the field, weekly updating and interpretation of geological data, elaboration of weekly and monthly reports. Works to be billed monthly as a lump sum divided on a percentage basis with regard to the contractor’s schedule of works. | flat rate | 1 |  | 0
3.3 | Ongoing soil sampling in the field and conducting of laboratory tests with elaboration of monthly reports.
3.3.1 | Basic laboratory testing of soil
3.3.1.1 | Classification and description of material | unit | 45 |  | 0
SIST EN ISO 14688-2:2018, USCS
3.3.1.2 | Measurement with pocket penetrometer | unit | 45 |  | 0
SIST EN 1997-2:2007, BS 1377:Part 9:1990
3.3.1.3 | Natural moisture content | unit | 45 |  | 0
SIST EN ISO 17892-1:2015; SIST EN 1097-5:2008
3.3.1.4 | Bulk density | unit | 45 |  | 0
SIST EN ISO 17892-2:2015
3.3.1.5 | Specific mass | unit | 45 |  | 0
SIST EN ISO 17892-3:2016
3.3.1.6 | Analysis of particle size distribution | unit | 45 |  | 0
SIST EN 933-1:2012
3.3.1.7 | Atterberg plastic limits | unit | 45 |  | 0
SIST EN ISO/TS 17892-12:2004
3.3.1.8 | Uniaxial compressive strength (solid silts) | unit | 45 |  | 0
SIST EN ISO 17892-7:2018
3.3.1.9 | Bulk modulus up to 3200 kPa with unloading curve | unit | 45 |  | 0
SIST EN ISO 17892-5:2017
3.3.1.10 | Swell testing | unit | 45 |  | 0
SIST EN ISO 17892-5:2017
3.3.1.11 | Water permeability (variable hydraulic gradient, 2 stages) | unit | 45 |  | 0
SIST EN ISO 17892-11:2019
3.3.1.12 | Direct shear | unit | 45 |  | 0
SIST-TS CEN ISO/TS 17892-10:2004
3.3.2 | Additional laboratory testing of soil
3.3.2.1 | Triaxial shear testing, undrained and drained shear strength | unit | 10 |  | 0
SIST EN ISO 17892-9:2018
3.3.2.2 | Bender element testing | unit | 10 |  | 0
manufacturer’s instructions
3.3.2.3 | Dynamic torsional triaxial test | unit | 10 |  | 0
JGS 0543-2000
3.3.2.4 | Water absorption (Enslin) | unit | 10 |  | 0
DIN 18132:2012-04
3.3.2.5 | Suction measurements with WP4 (10 points) | unit | 10 |  | 0
manufacturer’s instructions
3.3.2.6 | Suction measurements with tensiometer | unit | 10 |  | 0
manufacturer’s instructions
3.3.2.7 | Humosity | unit | 5 |  | 0
SIST EN 1744-1:2010+A1:2013 (15.1)
3.3.2.8 | Proctor strength and compressive strength | unit | 5 |  | 0
SIST EN 13286-2:2010/AC:2013
3.3.2.9 | Water permeability (constant hydraulic gradient in 3AX) | unit | 30 |  | 0
SIST EN ISO 17892-11:2019
3.3.2.10 | Direct shear testing for gravelly layers in a large shear cell | unit | 3 |  | 0
BS 1377:Part 7:1990 Point 5
3.3.2.11 | Mineralogical and petrographic soil analysis with an emphasis on the presence of potentially harmful components that could cause degradation of concrete and swelling | unit | 15 |  | 0
microscopic analysis, X-ray powder diffraction
3.3.2.12 | Aggressiveness of water on concrete | unit | 15 |  | 0
SIST EN 13286-206: 2013
3.4 | Elaboration of monthly reports on sampling and laboratory testing | flat rate | 1 |  | 0
3.5 | Creation of a 3D geological model, real-time imaging of silo excavation faces with laser scanning and data processing. Data capture from existing boreholes (8 units) in the monitoring area. Scanning should be done with a guaranteed spatial resolution of points of less than 1 cm. | flat rate | 1 |  | 0
3.6 | Elaboration of a final geological report after completion of all earthworks and geotechnical works, to include ongoing geological monitoring, monthly reports, data analysis and interpretation of the 3D geological model. | set | 1 |  | 0
| TOTAL MONITORING DURING CONSTRUCTION: |  |  |  | 0

## 2.f_RECAPITULATION
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository Facilities – Phase 2
SET: | A.6_L2
EXTERIOR ARRANGEMENTS – Phase 2
RECAPITULATION OF CONSTRUCTION WORK COSTS
Note:
The inventory envisages that the Phase 2 facilities will be constructed at the same time as the Phase 1 facilities.
All preparatory works, construction site organisation, earthworks and monitoring during construction are therefore inventoried and costed in the Phase 1 inventory.
A.6.2 | EXTERIOR ARRANGEMENTS | Value (EUR)
1. | STORM WATER DRAINAGE SYSTEM (Mc) | 0
2. | CLEAN STORM WATER DRAINAGE SYSTEM (Ms) | 0
3. | INDUSTRIAL WASTEWATER DRAINAGE SYSTEM (T) | 0
4. | TRANSPORT AREAS | 0
5. | TRAFFIC SIGNS AND MARKINGS | 0
| TOTAL | 0

## 2.f_1 Storm water drainage syst
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository Facilities – Phase 2
SET: | A.6_L2
4. | STORM WATER DRAINAGE SYSTEM (Mc)
Position | Description | Unit | Quantity | Price | Value
General provisions:
This inventory covers earthworks below the fertile soil/humus layer. The excavation of fertile soil is covered in the earthworks section. Other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the construction of the repository plateau areas.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 48 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III–IV – gravel | m3 | 45 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 43 |  | 0
4. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 14 |  | 0
5. | Removal of surplus material from the sewer excavation to a depot to be provided by the contractor, with all disposal costs | m3 | 31 |  | 0
6. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 19 |  | 0
7. | Supply and installation of C20/25 concrete as an anti-flotation casing for PE trenches Concrete encasing procedures to be carried out according to the trench manufacturer’s instructions. | m3 | 1 |  | 0
8. | Supply and installation of sewer system PE pipes, peripheral stiffness SN 8 kN/m2, material PE100 on prepared substrate with electrofusion jointing, pipe surface cleaning, cutting and all ancillary works, materials and transfers
a. | – PE DN 160 – connections to drains | m | 7 |  | 0
b. | – PE DN 200 | m | 36 |  | 0
9. | Construction of PE sewer trenches with treated bottom, constructed ditch, set of rings for cover installation and all ancillary works, concrete and mortar installation and transfer to installation site, properly concreted where necessary to prevent settlement of the trench or damage due to flotation under load
a. | – trench DN 800 at depth of up to 1 m | unit | 1 |  | 0
b. | – trench DN 800 at depth of 1–1.5 m | unit | 1 |  | 0
10. | Supply and installation of cast-iron covers fi60 cm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site
| – Class D (400 kN) | unit | 2 |  | 0
11. | Complete construction of under-curb storm drains (DN500 PE trench) to a depth of up to 2 m with a channel cover with a bearing capacity of 125 kN suitable for PE shafts | unit | 2 |  | 0
12. | Construction of inspection shafts, trench inlets and other sewer installations, including bed preparation, sealing of joints, etc. for all pipe diameters | unit | 8 |  | 0
13. | Inspection of sewers with a camera and preparation of a report | m | 48 |  | 0
14. | Testing of sewers and trenches for permeability, functionality and watertightness prior to backfilling of sewer pipes, in accordance with the law and applicable regulations (SIST EN 1610) | m | 48 |  | 0
| T O T A L STORM WATER DRAINAGE SYSTEM (Mc) |  |  |  | 0

## 2.f_2 Clean storm water drainag
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository Facilities – Phase 2
SET: | A.6_L2
5. | CLEAN STORM WATER DRAINAGE SYSTEM (Ms)
Position | Description | Unit | Quantity | Price | Value
General provisions:
This inventory covers earthworks below the fertile soil/humus layer. The excavation of fertile soil is covered in the earthworks section. Other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the construction of the repository plateau areas.
This inventory describes the works for sewer section Ms 1.3 – Phase 2.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 40 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III–IV – gravel | m3 | 34 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 36 |  | 0
4. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 13 |  | 0
5. | Removal of surplus material from the sewer excavation to a depot to be provided by the contractor, with all disposal costs | m3 | 21 |  | 0
6. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 19 |  | 0
7. | Supply and installation of sewer system PE pipes, peripheral stiffness SN 8 kN/m2, material PE100 on prepared substrate with electrofusion jointing, pipe surface cleaning, cutting and all ancillary works, materials and transfers
a. | – PE DN 200 | m | 39 |  | 0
8. | Construction of PE sewer trenches with treated bottom, constructed ditch, set of rings for cover installation and all ancillary works, concrete and mortar installation and transfer to installation site, properly concreted where necessary to prevent settlement of the trench or damage due to flotation under load
a. | – trench DN 1000 at depth of 1–1.5 m | unit | 2 |  | 0
9. | Supply and installation of cast-iron covers fi60 cm, including installation of bedding, installation of a 1:3 cement mortar frame and other ancillary works, mortar application and delivery to installation site
a. | – Class D (400 kN) | unit | 1 |  | 0
b. | – Class B (125 kN) | unit | 1 |  | 0
10. | Construction of inspection shafts, trench inlets and other sewer installations, including bed preparation, sealing of joints, etc. for all pipe diameters | unit | 5 |  | 0
11. | Testing of sewers and trenches for permeability, functionality and watertightness prior to backfilling of sewer pipes, in accordance with the law and applicable regulations (SIST EN 1610) | m | 40 |  | 0
| T O T A L CLEAN STORM WATER DRAINAGE SYSTEM (Ms) |  |  |  | 0

## 2.f_3 Industrial wastewater dra
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository Facilities – Phase 2
SET: | A.6_L2
6. | INDUSTRIAL WASTEWATER DRAINAGE SYSTEM (T)
Position | Description | Unit | Quantity | Price | Value
General provisions:
This inventory covers earthworks below the fertile soil/humus layer. The excavation of fertile soil is covered in the earthworks section. Other works, such as the arrangement of the superstructure of the transport areas and the final arrangement of the plateau, are fully included in the construction of the repository plateau areas.
The supply and installation of a stainless-steel sheathed pipe (INOX DN 100, fi 200 mm) is included in the mechanical installation plan. The same applies to the leak test and all other supporting documentation.
1. | Stakeout of the route of the sewer system and trenches in accordance with the stakeout data in the project – flat terrain | m | 15 |  | 0
2. | Excavation of trenches for sewer pipes with expansion of the excavation for trenches, trench inlets and other sewer structures with removal of material to the edge of the excavation – Excavation in Category III–IV – gravel | m3 | 16.5 |  | 0
3. | Levelling of the bottom of the channel (precision +-1 cm) in the projected longitudinal slope with manual excavation, average 0.05 m3/m2, and reinforcement | m2 | 8.8 |  | 0
4. | Supply and installation of a sand bed (0–8 mm granulation) for the laying of sewer pipes in the projected longitudinal slope, with reinforcement Production according to the pipe manufacturer’s instructions – thickness 15 cm | m3 | 2.2 |  | 0
5. | Delivery and backfilling of sewer pipes with gravel sand material of (0–16 mm granulation) at a height of 30 cm above the top of the pipe, with reinforcement Production according to the pipe manufacturer’s instructions | m3 | 5 |  | 0
6. | Backfilling of the sewer pipes with selected material from the excavation in 20 cm layers with compaction and rolling | m3 | 8.5 |  | 0
7. | Removal of surplus material from the sewer excavation to the embankment within the site, together with loading, rolling and installation into the embankment | m3 | 8 |  | 0
8. | Supply and installation of C20/25 concrete for concrete bedding and pipe concreting for protection under road surfaces at minimum depths and at crossings with other utility lines and pipes | m3 | 1 |  | 0
| T O T A L INDUSTRIAL WASTEWATER DRAINAGE SYSTEM |  |  |  | 0

## 2.f_4. Transport areas
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
7. | TRANSPORT AREAS
Position | Description | Unit | Quantity | Price | Value
General provisions:
All embankment works are invoiced according to the volume of earth in as-built state. The calculation of quantities is based on profiles taken before and after backfilling. For the purpose of billing for the works, the costs of the surveying works are included in the price of the embankment works.
GRAVEL BUFFER
1. | Preparation of the base for the gravel buffer by levelling to +-3 cm and consolidation to a minimum compaction of Ev2=80 MN/m2 | m2 | 564 |  | 0
2. | Supply and mechanical installation of 0/32 mm buffer material, a mixture of crushed stone granules, together with compaction and levelling of the subgrade +- 1 cm (calculated as per the compacted state)
a. | – gravel buffer of a minimum thickness of 40 cm – Road 1, consolidation to a minimum of Ev2 = 120 MN/m2. | m3 | 203 |  | 0
b. | – gravel buffer of a minimum thickness of 40 cm – Road 2, consolidation to a minimum of Ev2 = 80 MN/m2. | m3 | 41 |  | 0
c. | – gravel buffer of a minimum thickness of 30 cm – footpaths, pavements, consolidation to a minimum of Ev2 = 80 MN/m2. | m3 | 5 |  | 0
d. | – gravel buffer of a minimum thickness of 25 cm – concrete floor, consolidation to a minimum of Ev2 = 80 MN/m2. | m3 | 2 |  | 0
e. | – gravel buffer of a thickness of approx. 55 cm – backfill at buildings under gravel to a minimum of Ev2 = 60 MN/m2. | m3 | 16 |  | 0
ASPHALT WORKS
3. | Spraying of gravel subgrade with bitumen for the asphalt layer to ensure better bonding | m2 | 460 |  | 0
4. | Supply and mechanical laying of a load-bearing layer of bituminised mix on a prepared buffer base of quality AC 32 base PmB 25/55-65 A2, 10 cm thick – Road 1 | m2 | 460 |  | 0
5. | Supply and laying of a wear-resistant barrier of bituminised mix AC surf 11 PmB 45/80-65 A2, 4 cm thick – Road 1 | m2 | 460 |  | 0
6. | Supply and mechanical laying of a load-bearing layer of bituminised mix on a prepared buffer base of quality AC 16 base B 70/100 A4, 5 cm thick – Road 2 | m2 | 92 |  | 0
7. | Supply and laying of a wear-resistant barrier of bituminised mix AC surf 8 B 70/100 A4, 3 cm thick – Road 2 | m2 | 92 |  | 0
8. | Supply and laying of a wear-resistant barrier of bituminised mix AC surf 8 B 70/100 A5, 4 cm thick – pavements | m2 | 12 |  | 0
KERBS
9. | Supply, spread and installation of concrete kerbs in a C12/15 concrete base with cement mortar grouting of the joints, together with earthworks and all ancillary works and transfers Deepened and raised kerbs
a. | – dimensions 15/25/100 cm | m | 76 |  | 0
b. | – dimensions 15/25/100 cm – curve | m | 24 |  | 0
c. | – dimensions 8/20/100 cm – curve | m | 16 |  | 0
d. | – dimensions 8/20/100 cm – adjacent to TB – Phase 2 | m | 50 |  | 0
GRAVEL ADJACENT TO BUILDINGS
10. | Spreading of gravel (32 mm granulation) to a thickness of 10cm adjacent to the TB. | m2 | 20 |  | 0
CONCRETE FLOORS
11. | The external reinforced concrete pavement, 25 cm thick, is made of reinforced concrete with specification C30/37 XC4/XF4/XD2 Dmax 16 mm (OPZT S25). Polypropylene fibres, 10–12 mm in length (0.91 kg/m3), are added to the concrete mix. The concrete mix must use a quarried stone aggregate that is grey in colour. After pouring and compaction, the surface of the concrete is manually processed (trowelled), with all the necessary inclines being executed. Cutting of virtual dilatations is done according to the architectural or reinforcement plan of dilatations. The reinforcement is placed in each field separately.
After suitable curing, the concrete surface is machine processed, first by coarse grinding approximately 4 mm deep, and then by bush-hammering. After grinding, all larger holes in the concrete are filled with a suitable mortar (freeze-resistant XF4), which must be of a suitable colour. Only after filling is the concrete bush-hammered. Before execution, a test field of at least 1 m2 in area must be produced using the same materials and the chosen treatment process. The test field and the appearance of the surface after treatment are subject to the architect’s approval. The test field is repeated as necessary until the right appearance has been achieved and approval has been given by the architect.
a. | ~ preparation of the substrate for the installation of the waterproofing membrane – fine grading of the gravel substrate (precision +-1 cm) with reinforcement to a minimum compactness of Ev2=80 MPa | m2 | 4 |  | 0
b. | ~ waterproofing membrane such as Gefitas PE 3/300 | m2 | 4 |  | 0
c. | ~ concrete C30/37 XC4/XF4/XD2 Dmax 16 mm with microfibres | m3 | 1 |  | 0
d. | ~ bush-hammering | m2 | 4 |  | 0
e. | ~ protection of the bush-hammered surface with a coating such as Pieri Early Protect VBA immediately after surface treatment is completed | m2 | 4 |  | 0
12. | Complete dilatation of the contact of the concrete slabs with the installation of expanded polyethylene filler, 10 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edges at an angle of 45° and to a width of 1 cm | m | 3.5 |  | 0
13. | Complete implementation of a gap along the curb, to be filled with expanded polyethylene filler, 10 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edge of the concrete slab, width 1 cm, 45° angle | m | 3.5 |  | 0
14. | Complete construction of the expansion joint along the building with the installation of expanded polyethylene filler, 10 mm thick (e.g. Aerofil 2) and sealed with putty (e.g. Geocel PRO 592) Grinding of the upper edge of the concrete slab, width 1 cm, 45° angle | m | 1 |  | 0
15. | Supply and installation of a 70/30/4 mm stainless steel angle iron, with anchors at 50 cm intervals and its fixing into the formwork prior to concreting | m | 1 |  | 0
16. | Supply, machining and manual assembly of concrete steel reinforcement of various profiles and B500B reinforcement grids | kg | 140 |  | 0
17. | Formwork of floor slab edges; formwork, formwork removal and cleaning:
| – formwork 25 cm high – flat part | m2 | 2 |  | 0
| T O T A L TRANSPORT AREAS: |  |  |  | 0

## 2.f_5. Traffic signs and markin
Contractor: | ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
8. | TRAFFIC SIGNS AND MARKINGS
Position | Description | Unit | Quantity | Price | Value
1. | Production of thin-film marking with single-component white paint, thickness of dry matter layer 300 microns
a | line 5111 (solid dividing line), line width 15 cm | m | 10 |  | 0
b. | line 5112 (solid border line), line width 15 cm | m | 11 |  | 0
c. | line 5121 (1-1-1), broken dividing line, w=15 cm | m | 61 |  | 0
d. | line 5122, solid border line, width 15 cm, w=10 cm | m | 30 |  | 0
e. | line 5212, solid wide transversal line, grid 100 x 50 cm, w=50 cm | m | 7.5 |  | 0
f. | line 5231, pedestrian crossing | m2 | 35 |  | 0
2. | Production of marking with symbols and single-component white paint, thickness of dry matter layer 300 microns
a. | symbol 5604, junction with main road | unit | 1 |  | 0
b. | symbol 5234 pedestrian pathway | unit | 5 |  | 0
3. | Construction of a foundation for traffic signs, concrete C 12/15, depth 80 cm deep, diameter 40 cm | unit | 1 |  | 0
4. | Supply and installation of a traffic sign post made of hot-dip galvanised tubular steel
| – fi 64 mm, length 3,500 mm | unit | 1 |  | 0
5. | Supply and fixing of a round traffic sign, aluminium sheet base
| – 2101; triangle – junction/intersection with main road | unit | 1 |  | 0
6. | Production of kerb markings with ground marking tape, red-white marking, anti-slip, 75 mm wide, suitable for outdoor use, self-adhesive | m | 7 |  | 0
| T O T A L TRAFFIC SIGNS AND MARKINGS: |  |  |  | 0

## Table of prices
Contractor: ARAO
Facility: Vrbina LILW Repository, Krško
LOT 2 – Repository facilities
SET: | A.6_L2
CALCULATION BASES FOR DETERMINATION OF UNIT PRICES
| Description | unit | Price per unit (EUR)
1. | WORKS
1.1 | Graduate engineer | hour
1.2 | Technician | hour
1.3 | Highly skilled worker | hour
1.4. | Skilled worker | hour
1.5. | Unskilled worker | hour
2. | TRANSPORT
2.1 | Trailer up to 10 t | km
2.2 | Trailer 10–20 t | km
2.3 | Truck up to 5 t | km
2.4 | Truck 5–10 t | km
2.5 | Truck over 10 t | km
2.6 | Truck with crane up to 10 t | km
2.7 | Truck with crane over 10 t | km
2.8 | Tipper truck up to 8 t | km
2.9 | Tipper truck 8–12 t | km
2.10 | Tipper truck 12–20 t | km
2.11 | Tipper truck over 20 t | km
3. | EXCAVATION AND LOADING
3.1 | Hydraulic excavator up to 0.5 m3 | hour
3.2 | Hydraulic excavator 0.5–1 m3 | hour
3.3 | Hydraulic excavator over 1 m3 | hour
3.4 | Excavator for the execution of driven piles | hour
3.5 | Bulldozer 110 kW | hour
3.6 | Bulldozer 170 kW | hour
3.7 | Trencher up to 0.50 m3 | hour
3.8 | Loader 0.80–1.20 m3 | hour
3.9 | Loader 1.50–2.00 m3 | hour
4. | ROLLERS
4.1 | Vibratory roller up to 10 t | hour
4.2 | Vibratory roller over 10 t | hour
4.3 | Rubber roller up to 10 t | hour
4.4 | Rubber roller over 10 t | hour
4.5 | Vibratory rammer | hour
5. | CONCRETE WORKS
5.1 | Automatic mixer up to 6 m3 | hour
5.2 | Automatic mixer over 6 m3 | hour
5.3 | Mobile concrete pump up to 20 m3/h | hour
5.4 | Mobile concrete pump over 20 m3/h | hour
5.5 | Concrete vibrators | hour
5.6 | Shotcrete set | hour
6. | CRANES AND LIFTING GEAR
6.1 | – up to 10 t | hour
6.2 | – 10–15 t | hour
6.3 | – 10–15 t | hour
6.4 | – over 20 t | hour
6.5 | Truck crane up to 10 t | hour
6.6 | Mobile crane 10 to 40 t | hour
6.7 | Mobile crane 40 to 100 t | hour
6.8 | Mobile crane 100 to 300 t | hour
7. | COMPRESSORS AND GENERATORS
7.1 | Compressor up to 5 m3/min | hour
7.2 | Compressor 5–15 m3/min | hour
7.3 | Compressor over 15 m3/min | hour
7.4 | Portable generator up to 20 kVA | hour
7.5 | Portable generator 20–50 kVA | hour
7.6 | Portable generator 50–150 kVA | hour
7.7 | Portable generator over 150 kVA | hour
8. | MISCELLANEOUS
8.1 | Water pump up to 3 kW | hour
8.2 | Water pump 3–10 kW | hour
8.3 | Water pump 10–50 kW | hour
8.4 | Welding kit | hour
9. | Transporting of excavated material over distances:
9.1 | 0.5 km | m3
9.2 | 1 km | m3
9.3 | 2 km | m3
9.4 | 3 km | m3
9.5 | 4 km | m3
9.6 | 5 km | m3
9.12 | 10 km | m3
9.17 | 15 km | m3
9.22 | 20 km | m3