TECHNICAL SPECIFICATION

# Spare Charging Pump Motor

# Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG01, Rev.1

KRŠKO NUCLEAR POWER PLANT

APPENDIX A6

Revision 0

NUCLEAR SAFETY RELATED

TABLE OF CONTENT

A6.    Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG01, Rev.0	1

| # A6. Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG01, Rev.0 |  |  |  |
| --- | --- | --- | --- |
|  | Parameter Value of Existing motor | Parameter Value of Proposed motor | Comment |
| Vendor | Westinghouse |  | Click or tap here to enter text. |
| Frame | 6809H | Click or tap here to enter text. | Click or tap here to enter text. |
| Model | HSDP | Click or tap here to enter text. | Click or tap here to enter text. |
| NEMA Design | A | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed lifetime | 40 years | Click or tap here to enter text. | Click or tap here to enter text. |
| Enclosure | Drip Proof | Click or tap here to enter text. | Click or tap here to enter text. |
| Power | 600 HP | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Voltage | 6000 Volts | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Current | 50 Amperes | Click or tap here to enter text. | Click or tap here to enter text. |
| Speed | 2976 RPM | Click or tap here to enter text. | Click or tap here to enter text. |
| Frequency | 50 Hertz | Click or tap here to enter text. | Click or tap here to enter text. |
| Duty | Continuous | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotation | Clockwise | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed Ambient Temperature | 50°C | Click or tap here to enter text. | Click or tap here to enter text. |
| Temperature Rise | 80°C | Click or tap here to enter text. | Click or tap here to enter text. |
| Service Factor | 1.15 | Click or tap here to enter text. | Click or tap here to enter text. |
| Class of insulation | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Insulation Treatment | Thermalastic Epoxy | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearings size | 3.5''x4.5'' (split sleeve) | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing Lubrication (type/grade) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing L10h life | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Normal Bearing Operational Temperature | 85°C (max) | Click or tap here to enter text. | Click or tap here to enter text. |
| Space heaters | 400 V, 1 phase, 238 W | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Current | 555 A | Click or tap here to enter text. | Click or tap here to enter text. |
| Locket Rotor KVA code | L | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Torque | 1096 lb∙ft | Click or tap here to enter text. | Click or tap here to enter text. |
| Starting Torque % F.L. | 278 | Click or tap here to enter text. | Click or tap here to enter text. |
| Pull-Out Torque % F.L. | 514 | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Torque % F.L. | 278 | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Efficiency | 93.9 | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Efficiency | 93.2 | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Efficiency | 91.5 | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Power Factor | 91.0 | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Power Factor | 87.8 | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Power Factor | 80.1 | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Power Factor | 31.6 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at Rated Voltage and connected Load | 1.84 sec | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator resistance (Line to Line) at 25°C | 0.9974 ohms | Click or tap here to enter text. | Click or tap here to enter text. |
| Minimum Starting Voltage | (80%) 4800V | Click or tap here to enter text. | Click or tap here to enter text. |
| Load Inertia Referred to Motor Shaft | 165 lb∙ft2 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at minumum Voltage and Connected Load | 4.5 sec | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor weight | 1506 lbs | Click or tap here to enter text. | Click or tap here to enter text. |
| Motor weight | 6200 lbs | Click or tap here to enter text. | Click or tap here to enter text. |
| Type sealed insulation system | Thermalastic Epoxy | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Insulation Materials and Method of Impregnation | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Coil Turn Insulation and Description | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Winding Coil Surge Withstand Capability (Peak Volts/Rise Time) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Temperature Rise (Temp. Detector/Resistance) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| First Rotor Lateral Critical Speed | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Stator Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Rotor Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Bar material | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Shorting Ring Material | / | Click or tap here to enter text. | Click or tap here to enter text. |