TECHNICAL SPECIFICATION

# Replacement Motor for

# CIAPCS01, CIAPCS02 Pumps

# Compliance Motor Matrix to NEK Technical Specification

# No. SP-ES1373, Rev.2

KRŠKO NUCLEAR POWER PLANT

Revision 2

NUCLEAR SAFETY RELATED

TABLE OF CONTENT

Compliance Motor Matrix to NEK Technical Specification  No. SP-ES1373, Rev.2	1

| # Compliance Motor Matrix to NEK Technical Specification No. SP-ES1373, Rev.2 |  |  |  |
| --- | --- | --- | --- |
| Parameter | Parameter Value of Existing motor | Parameter Value of Proposed motor | Comment |
| Vendor | Westinghouse | Click or tap here to enter text. | Click or tap here to enter text. |
| Frame | 5008-H | Click or tap here to enter text. | Click or tap here to enter text. |
| Type | LLD | Click or tap here to enter text. | Click or tap here to enter text. |
| NEMA Design | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed lifetime | 40 years | Click or tap here to enter text. | Click or tap here to enter text. |
| Enclosure | Drip proof | Click or tap here to enter text. | Click or tap here to enter text. |
| Power | 300 HP | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Voltage | 380 V | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Current | 394 Amps | Click or tap here to enter text. | Click or tap here to enter text. |
| Speed | 2958 rpm | Click or tap here to enter text. | Click or tap here to enter text. |
| Frequency | 50 Hz | Click or tap here to enter text. | Click or tap here to enter text. |
| Duty | Continuous | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotation | CW | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed Ambient Temperature | 50°C | Click or tap here to enter text. | Click or tap here to enter text. |
| Temperature Rise | 80°C | Click or tap here to enter text. | Click or tap here to enter text. |
| Service Factor | 1.15 | Click or tap here to enter text. | Click or tap here to enter text. |
| Class of insulation | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Insulation Treatment | Thermalastic Epoxy | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearings size | 3.0'' x 4.0'' (split sleeve) | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing Lubrication (type/grade) | Oil | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing L10h life | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Normal Bearing Operational Temperature | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Space heaters | Wraparound 380 V, 0.53 Amps, 202Watt | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Current | 2337 Amps | Click or tap here to enter text. | Click or tap here to enter text. |
| Locket Rotor KVA code | F | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Torque | 532 lbft | Click or tap here to enter text. | Click or tap here to enter text. |
| Starting Torque % F.L. | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Maximum Torque % F.L. | 257 | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Torque % F.L. | 115 | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Efficiency | 93.5 % | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Efficiency | 93.7 % | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Efficiency | 93.1 % | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Power Factor | 92.4 | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Power Factor | 92.0 | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Power Factor | 89.1 | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Power Factor | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at Rated Voltage and connected Load | 1.37 sec | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator resistance (Line to Line) at 25°C | 0.0.16 ohms | Click or tap here to enter text. | Click or tap here to enter text. |
| Minimum Starting Voltage | 304 V (80%) | Click or tap here to enter text. | Click or tap here to enter text. |
| Load Inertia Referred to Motor Shaft | 15.0 lb∙ft2 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at minimum Voltage and Connected Load | 2.7 (allowed 5 sec) | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor weight | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Motor weight | 2350 lbs | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Insulation Materials and Method of Impregnation | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Coil Turn Insulation and Description | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Winding Coil Surge Withstand Capability (Peak Volts/Rise Time) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Temperature Rise (Temp. Detector/Resistance) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| First Rotor Lateral Critical Speed | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Stator Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Rotor Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Bar material | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Shorting Ring Material | / | Click or tap here to enter text. | Click or tap here to enter text. |