TECHNICAL SPECIFICATION

# Spare Safety Injection Pump Motor

# Compliance Motor Matrix to NEK Technical Specification

# No.TS34-VNMG09, Rev.1

KRŠKO NUCLEAR POWER PLANT

APPENDIX A5

Revision 1

NUCLEAR SAFETY RELATED

TABLE OF CONTENT

A5.    Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG09, Rev.1	1

| # A5. Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG09, Rev.1 |  |  |  |
| --- | --- | --- | --- |
| Parameter | Parameter Value of Existing motor | Parameter Value of Proposed motor | Comment |
| Vendor | Westinghouse | Click or tap here to enter text. | Click or tap here to enter text. |
| Frame | 6808S | Click or tap here to enter text. | Click or tap here to enter text. |
| Model | HSDP | Click or tap here to enter text. | Click or tap here to enter text. |
| NEMA Design | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed lifetime | 40 | Click or tap here to enter text. | Click or tap here to enter text. |
| Enclosure | Drip-Proof | Click or tap here to enter text. | Click or tap here to enter text. |
| Power | 800 HP | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Voltage | 6000 V | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Current | 67 A | Click or tap here to enter text. | Click or tap here to enter text. |
| Speed | 1479 RPM | Click or tap here to enter text. | Click or tap here to enter text. |
| Frequency | 50 Hz | Click or tap here to enter text. | Click or tap here to enter text. |
| Duty | Continuous | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotation | CW | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed Ambient Temperature | 50 °C | Click or tap here to enter text. | Click or tap here to enter text. |
| Temperature Rise | 80 °C | Click or tap here to enter text. | Click or tap here to enter text. |
| Service Factor | 1.15 | Click or tap here to enter text. | Click or tap here to enter text. |
| Class of insulation | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Insulation Treatment | Thermalastic Epoxy | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearings size | 4.5’’ (sleeve) | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing Lubrication (type/grade) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing L10h life | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Normal Bearing Operational Temperature | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Space heaters | 120 V, 1 phase, 240 W | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Current | 416 A | Click or tap here to enter text. | Click or tap here to enter text. |
| Locket Rotor KVA code | F | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Torque | 2840 ftlb | Click or tap here to enter text. | Click or tap here to enter text. |
| Starting Torque % F.L. | 115 % | Click or tap here to enter text. | Click or tap here to enter text. |
| Pull-Out Torque % F.L. | 261 % | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Torque % F.L. | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Efficiency | 93.9 % | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Efficiency | 94.2 % | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Efficiency | 93.9 % | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Power Factor | 91.5 | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Power Factor | 90.8 | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Power Factor | 87.2 | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Power Factor | 28.7 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at Rated Voltage and connected Load | 1.6 sec | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator resistance (Line to Line) at 25°C | 1.3767 Ω | Click or tap here to enter text. | Click or tap here to enter text. |
| Minimum Starting Voltage | (80%) 4800V | Click or tap here to enter text. | Click or tap here to enter text. |
| Load Inertia Referred to Motor Shaft | 424 lb∙ft2 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at minimum Voltage and Connected Load | 3.4 sec (5 sec required) | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor weight | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Motor weight | 5900 lbs | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Insulation Materials and Method of Impregnation | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Coil Turn Insulation and Description | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Winding Coil Surge Withstand Capability (Peak Volts/Rise Time) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Temperature Rise (Temp. Detector/Resistance) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| First Rotor Lateral Critical Speed | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Stator Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Rotor Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Bar material | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Shorting Ring Material | / | Click or tap here to enter text. | Click or tap here to enter text. |