TECHNICAL SPECIFICATION

# Spare Component Cooling Pump Motor

# Compliance Motor Matrix to NEK Technical Specification

# No. TS34-VNMG10, Rev.1

KRŠKO NUCLEAR POWER PLANT

APPENDIX A4

Revision 1

NUCLEAR SAFETY RELATED

TABLE OF CONTENT

A4.     Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG10, Rev.1	1

| # A4. Compliance Motor Matrix to NEK Technical Specification No. TS34-VNMG10, Rev.1 |  |  |  |
| --- | --- | --- | --- |
| Parameter | Parameter Value of Existing motor | Parameter Value of Proposed motor | Comment |
| Vendor | Westinghouse | Click or tap here to enter text. | Click or tap here to enter text. |
| Frame | 6808-S | Click or tap here to enter text. | Click or tap here to enter text. |
| Model | HSDP | Click or tap here to enter text. | Click or tap here to enter text. |
| NEMA Design | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed lifetime | 40 | Click or tap here to enter text. | Click or tap here to enter text. |
| Enclosure | Drip-Proof | Click or tap here to enter text. | Click or tap here to enter text. |
| Power | 500 HP | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Voltage | 6000 V | Click or tap here to enter text. | Click or tap here to enter text. |
| Nominal Current | 41 A | Click or tap here to enter text. | Click or tap here to enter text. |
| Speed | 1486 RPM | Click or tap here to enter text. | Click or tap here to enter text. |
| Frequency | 50 Hz | Click or tap here to enter text. | Click or tap here to enter text. |
| Duty | Continuous | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotation | CW | Click or tap here to enter text. | Click or tap here to enter text. |
| Designed Ambient Temperature | 50 °C | Click or tap here to enter text. | Click or tap here to enter text. |
| Temperature Rise | 80 °C | Click or tap here to enter text. | Click or tap here to enter text. |
| Service Factor | 1.15 | Click or tap here to enter text. | Click or tap here to enter text. |
| Class of insulation | B | Click or tap here to enter text. | Click or tap here to enter text. |
| Insulation Treatment | Thermalastic Epoxy | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearings size | 4.5’’ (sleeve) | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing Lubrication (type/grade) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Bearing L10h life | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Normal Bearing Operational Temperature | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Space heaters | 400 V, 1 phase | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Current | 252 A | Click or tap here to enter text. | Click or tap here to enter text. |
| Locket Rotor KVA code | F | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Torque | 1761 lb∙ft | Click or tap here to enter text. | Click or tap here to enter text. |
| Starting Torque % F.L. | 110 % | Click or tap here to enter text. | Click or tap here to enter text. |
| Pull-Out Torque % F.L. | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Torque % F.L. | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Efficiency | 94.0 % | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Efficiency | 94.7 % | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Efficiency | 94.8 % | Click or tap here to enter text. | Click or tap here to enter text. |
| Full Load Power Factor | 90.9 | Click or tap here to enter text. | Click or tap here to enter text. |
| 3/4 Load Power Factor | 91.1 | Click or tap here to enter text. | Click or tap here to enter text. |
| 1/2 Load Power Factor | 89.8 | Click or tap here to enter text. | Click or tap here to enter text. |
| Locked Rotor Power Factor | 0.287 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at Rated Voltage and connected Load | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator resistance (Line to Line) at 25°C | 3.24 Ω | Click or tap here to enter text. | Click or tap here to enter text. |
| Minimum Starting Voltage | (80%) 4800V | Click or tap here to enter text. | Click or tap here to enter text. |
| Load Inertia Referred to Motor Shaft | 99 lb∙ft2 | Click or tap here to enter text. | Click or tap here to enter text. |
| Acceleration Time at minimum Voltage and Connected Load | 6.03 sec | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor weight | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Motor weight | 6000 lbs | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Insulation Materials and Method of Impregnation | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Coil Turn Insulation and Description | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Winding Coil Surge Withstand Capability (Peak Volts/Rise Time) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Stator Winding Temperature Rise (Temp. Detector/Resistance) | / | Click or tap here to enter text. | Click or tap here to enter text. |
| First Rotor Lateral Critical Speed | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Stator Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Number of Rotor Slots | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Bar material | / | Click or tap here to enter text. | Click or tap here to enter text. |
| Rotor Shorting Ring Material | / | Click or tap here to enter text. | Click or tap here to enter text. |