DVB-T/T2 TRANSMITTERS

TECHNICAL REQUIREMENTS

AND

SPECIFICATIONS

FOR PUBLIC TENDER

No. JN-B1093

1	Introduction	4

1.1	Transmitter	4

1.2	Transposer	6

1.3	Repeater / Transposer	7

2	General	8

2.1	CE and EMC	8

2.2	Instructions for operation and maintenance	8

2.3	Noise	8

2.4	Internal Parts	8

2.5	External Parts	9

2.6	Transportation	9

2.7	Physical Dimensions	9

2.8	Connectors	9

2.9	Protection loop - interlock	9

2.10	Local interface	9

2.11	Remote interface	9

2.11.1	Web GUI	10

2.11.2	SNMP interface	10

2.12	Event Log	10

2.13	Warranty and after warranty remote support	11

3	Technology	11

3.1	Exciter	11

3.1.1	Input Signal	11

3.1.2	Pre-correction	11

3.1.2.1	Manual pre-correction	11

3.1.2.2	Adaptive pre-correction	12

3.1.3	TPS	12

3.1.4	MIP	12

3.1.5	Test Signal/PRBS	12

3.2	Tuner	12

3.3	Mixer	12

3.4	Echo canceller	12

3.5	Working Frequency	13

3.5.1	Frequency Range	13

3.5.2	Exciter IF stage	13

3.6	Synchronization	13

3.6.1	Frequency and time reference	13

3.6.2	Stability	13

3.6.3	Internal Reference	13

3.6.4	External Reference	13

3.6.5	Behavior In case of GPS Failure	14

3.6.6	SFN Propagation Delay Compensation	14

3.6.7	Dynamic Delay Compensation	14

3.6.8	Static Delay Compensation	14

3.7	Transmitter power	14

3.7.1	Output power	14

3.7.2	Nominal power	14

3.7.3	Power consumption	14

3.7.4	Stability	14

3.7.5	Return Loss	15

3.7.6	Efficiency	15

3.8	Output stage	15

3.9	Measurement/test points	15

3.9.1	Transport stream	15

3.9.2	RF test points	15

3.9.3	Isolation points	15

4	Quality of operation	16

4.1	Oscillator phase noise	16

4.2	Shoulder attenuation	16

4.3	Spectrum mask	17

4.4	Spurious emissions	17

4.5	Crest factor	17

4.6	Modulation error ratio / MER	17

4.6.1	Transmitter	17

4.6.2	Transposer	17

4.6.3	Repeater	17

5	Mains voltage	17

5.1	Connection to the mains supply	17

5.2	Switch-on	18

5.3	Uninterruptible Power Supply	18

5.3.1	Built-in power supply	18

5.3.2	External power supply	18

6	Input band-pass filter	18

7	Output channel band-pass filter	18

8	Dummy load	18

9	Cooling system	19

9.1	Liquid Cooling	19

9.2	Air Cooling	19

10	Control and monitoring	19

10.1	Event log	20

10.2	Local interface	21

10.3	Remote interface	22

10.3.1	Web GUI	22

10.3.2	SNMP/MIB	22

# Introduction

DVB-T/T2 transmitters, transposers and repeaters are devices that broadcast DVB-T/T2 signals in accordance with ETSI EN 300744. They must support operation in accordance with the technical specifications:

- ETSI EN 300744,

- EN TR 101190,

- EN TS 101191 and

- EN TR 101290.

This technical specification describes the following types of DVB-T/T2 devices:

## Transmitter

The incoming ASI stream is modulated into a DVB-T/T2 COFDM signal suitable for feeding one or more power amplifier stages.

Transmitter can consist of several functional stages combined into logical units:

- Exciter forms a DVB-T/T2 COFDM signal and modulates it on to the required carrier frequency

- GPS receiver provides reference timing signals

- UPS in case of power failure guarantees an uninterrupted operation of the exciter and control unit.

- Power amplifier stage amplifies the RF signal to a required level.

- Band-pass channel filter eliminates all unwanted signal components.

- Cooling system enables the operation of a transmitter in a proper temperature range by cooling the appropriate number of transmitter units.

- Control unit enables control and supervision of the whole transmitter.

Picture 1: Transmitter

There are two special transmitter configurations:

- 1+1 configuration where the whole transmitter with all sub-stages is doubled. In case of a transmitter failure the attached switch-over unit must switch operation to the currently standby transmitter. RF switch, dummy load and switching unit are part of this configuration.

Picture 2: Transmitter in 1+1 configuration

- Double drive configuration where only the exciter is doubled. In case of main exciter failure the system must switch over to the backup exciter without interruption of the output signal.

Picture 3: Transmitter in double drive configuration

## Transposer

The incoming RF signal is transposed to IF and then modulated on the required RF carrier frequency. This signal is then further amplified and filtered.

Transposer can consist of several functional stages combined into logical units:

- Tuner downmixes the incoming RF signal.

- Mixer transposes the IF signal onto the required carrier frequency.

- UPS in case of power failure guarantees uninterrupted operation of the device.

- Power amplifier stage amplifies the RF input signal to the required level.

- Band-pass channel filter eliminates all unwanted signal components.

- Cooling system enables the operation of a transmitter in a proper temperature range by cooling the appropriate number of transmitter units.

- Control unit enables control and supervision of the whole device.

Picture 4: Transposer

Special version of the transposer is re-transmitter.

Re-transmitter can consist of several functional stages combined into logical units:

- Tuner downmixes the incoming to the ASI signal.

- Modulator forms, from ASI signal, a DVB-T/T2 COFDM signal and modulates it on to the required carrier frequency

- UPS in case of power failure guarantees uninterrupted operation of the device.

- Power amplifier stage amplifies the RF input signal to the required level.

- Band-pass channel filter eliminates all unwanted signal components.

- Cooling system enables the operation of a transmitter in a proper temperature range by cooling the appropriate number of transmitter units.

- Control unit enables control and supervision of the whole device.

Picture 5: Transposer

## Repeater / Transposer

The incoming RF signal is transposed to IF. In a digital processing unit the signal is filtered (echo cancellation) and afterwards modulated on the same carrier frequency as the incoming signal. This signal is then further amplified and filtered.

Repeater must also be used as a Transposer. Switching between the Repeater and Transposer mode must be easily implemented through local and remote interface. Transposer must meet the specifications set out in paragraph 1.2.

Repeater can consist of several functional stages combined into logical units:

- Tuner downmixes the incoming RF signal.

- Echo canceller by use of adaptive filtering technologies removes echoes and other interference from the signal.

- Mixer transposes the IF signal onto the required carrier frequency.

- UPS in case of power failure guarantees uninterrupted operation of the device.

- Power amplifier stage amplifies the RF input signal to the required level.

- Band-pass channel filter eliminates all unwanted signal components.

- Cooling system enables the operation of a transmitter in a proper temperature range by cooling the appropriate number of transmitter units.

- Control unit enables control and supervision of the whole device.

Picture 6: Repeater / Transposer

# General

## CE and EMC

All equipment must meet technical requirements and standards in force in the Republic of Slovenia and related to electrical power supplies (230V / 400 V, 50 Hz), grounding and safety measures against electrical current strike:

- EN 50160,

- EN 60950,

- EN 61140 and

- Power factor - cos phi ≥ 0,95.

Guidance TSG-N-003 2008 – Safety actions against lightning must be fulfilled.

All offered equipment must also fulfill following Slovenian EMC standards:

- Technical EMC norm (ur.l.RS št. 132/06),

- EN 50081-1,

- EN 50082-2,

- EN 55022 and

- EN 55024.

## Instructions for operation and maintenance

Technical documentation needed for user’s daily work and maintenance must be in Slovene or English language. For technical documentation in electronic form Acrobat PDF format must be used. The documentation must reflect the current state of the equipment at the time of delivery. Documentation must include a user manual and service manual. By using this information, the user must be able to repair the equipment.

For each device it is required to provide one copy of documentation in printed and electronic form. If there are 2 or more devices of the same type, it is required to provide documentation in an according number of copies (not more than 3) in printed and electronic form for each type of device.

The technical documentation must comprise at least these items:

- Description of operation of the device and individual stages,

- Description of procedures for setting parameters and retuning of the device,

- Detailed schematic design of all stages of the device,

- List and description of all service exercises as required by the producer,

- Guidelines for repair and exchange of parts,

- Description of program functions and error messages,

- Protocols of all accessible control and supervisory interfaces,

- All system and administrative passwords,

- Declaration of all dangerous substances used and guidance for handling and removal.

The labels on the equipment must be in Slovene or English language.

## Noise

Under normal operating conditions, the noise level must not exceed 65 dBA measured at the height of 1,5 m and at 1 m distance from the device.

## Internal Parts

Parts of the device that are to be installed inside the building and will not be exposed to the weather conditions must operate under the following conditions:

- Temperature range: +5 °C ÷ 45 °C

- Relative humidity: <90%

- Input air temperature: <35 °C

all devices must meet the quality requirements in the temperature range from +10 °C to +35 °C at 1200 m above sea level.

## External Parts

Parts of the device, which are intended to be used outdoors, and thus exposed to the weather conditions, must operate under the following conditions:

- Temperature range: -30 °C ÷ 45 °C

- Relative humidity: 8 ÷ 100%

- Wind speed: 50 m/s

- Sun radiation power flux density: 1000 W/m2

## Transportation

During transportation a device in a non-working state must withstand:

- Temperature range: -40 °C ÷ 55 °C

- Relative humidity: 8 ÷ 100%

## Physical Dimensions

The depth of the whole device without the external cooling unit must be in a standard 19'' cabinet. The depth must not exceed 1m.

If a modular design of the transmitter is required is required and transmitter units are mounted in a cabinet, all spaces on the front side that are not completed must be closed with blind covers.

## Connectors

Only the following connector types can be used:

- BNC 75 Ω or 50 Ω,

- N,

- SMA, SMB, TNC,

- DIN 7/16,

- 7/8”, 1 5/8”,1/8" EIA,

- RJ45

For devices up to 200 W output power output RF connectors must be of type N-female or type DIN 7/16-female.

For transposers and repeaters the RF input connectors must be of type N-female.

## Protection loop - interlock

The device must be equipped with a connector for protective loop (interlock) functionality.

If the protection loop is opened the transmitter must be automatically switched off.

## Local interface

For fast device state recognition light indication according to following key must be used:

- Green – normal operation,

- Yellow – warning (abnormal operation without interruption of service),

- Red – fault (interruption of service).

The operator must be able to manage all parameters of the device by using the local interface, which consists of a display and keyboard.

## Remote interface

Remote control is based on IP over 10/100BaseT Ethernet network. Therefore, the device must have a LAN interface with RJ-45 connector according to the ISO 8877 specification.

The solutions to access the remote interface via the data network RJ45 connectors with separate VLAN is also allowed.

It must be possible to reset the IP, username and password in one of the following ways:

- Hidden switch or button on the device or

- Local interface or

- Serial interface RS232 and open terminal access without username and password or

- Remote interface.

It must be impossible to damage the device through the remote interface.

The remote control must have a web interface and an SNMP interface.

### Web GUI

The web user interface is the main remote interface. The single window web interface must provide complete monitoring and control over the device and all attached sub-devices. It must be possible to make software upgrades though the Web-GUI.

A two-level user interface with username and password must be implemented.

The web interface must allow simultaneous access for multiple users - 3 or more.

Transfer of each web site must be completed in less than 4 seconds.

Process data and status information inside the web interface must be refreshed in regular intervals (up to 15 seconds) with the possibility to disable or change.

It must be possible to save and restore device configuration by a single click.

An action history must be implemented to record user actions.

The web interface must allow browsing, resetting and saving the device log. In case of large logs, numbering with a maximum of 40 events per page must be implemented.

The entire device log should be easily (with one click) exported in CSV format.

The web interface must be fully functional in the latest versions of Firefox, Microsoft Edge and Chrome web browsers running on Linux or Windows operating system.

### SNMP interface

The UDP-based SNMP agent for monitoring and control must allow complete control over the device. All necessary MIB structures in ASN.1 format must be included. The SNMP must send messages (traps) on failure (urgentAlarmTrap), warning (WarningTrap) and other informational events (InfoTrap).

At the end of failure or warning the device must send an appropriate message (endofAlarmTrap). The web interface must allow changing at least following SNMP agent functionalities:

- At least four IP addresses for sending (Trap) notifications,

- Disable/enable of notification sending for various events (Alarm, Warning and Info).

The functions GET, SET, WALK and TRAP must be supported.

## Event Log

The device must record all events/warnings/alarms in the event log. Each log entry must be accompanied by the date and time of the start and end of the event. The Event Log must be organized as a circular buffer. In case the buffer is full, new entries must overwrite the oldest ones.

Event timestamps must be based on local time. Local time must be possible to set manually and automatically through synchronization via:

- GPS reference or

- Network time protocol – NTP or

- Transport stream (TDT)

The log must be able to store more than 1000 entries. The log entries must be listed in reverse order, from the youngest to the oldest. It must be possible to determine the cause of the device error by analyzing the event log.

The event log must not be deleted in case of power failure or when the device is turned off.

## Warranty and after warranty remote support

Remote access for support/maintenance will be enabled via the Internet. For this purpose, access will be provided to a computer on the internal network of the Contracting Authority, which will allow access to each device via a web browser (Firefox).

This will be implemented by a VNC session to a local computer. From this computer web access to devices will be possible.

# Technology

## Exciter

The exciter first modulates the input transport stream into a DVB-T/T2 COFDM signal on IF. This signal is then further transposed to the required RF output channel. In MFN mode the transmitter must be able to do zero padding and PCR correction if needed.

### Input Signal

The exciter must have two ASI transport stream inputs and two 100Base-TX (or 1000Base-T) RJ-45 ethernet connector.

Both ASI inputs must comprise to the electrical ASI specification EN 50083-9 Annex B. The data structure used must be in accordance with MPEG-2 transport stream specification ISO/IEC 13818-1. The transport stream packets length can be 188 or 204 bytes. The transport stream packets with a length of 204 bytes can include RS protection or just 16 null bytes. Inputs are asymmetrical of impedance Z = 75 Ω, BNC.

Data RJ45 network connector must comply with the ISO 8877 specification. Via the mentioned connectors exciter must allow the following functionality:

- Receiving packets based on VLAN tags according to the IEEE 802.1Q specification,

- TSoIP with forward error correction (FEC) of input signal according to the Pro-MPEG CoP#3 (SMPTE2022) specification.

Switching between inputs must be performed via an interface for local and remote control.

The transmitter must be switched off immediately if at least one of the following conditions occurs:

- No transport stream,

- Presence of synchronization failures,

- Data capacity is too high for the chosen transmission mode,

- There are discrepancies between the mip data and the setup in the transmitter.

When the error is gone the transmitter must be switched on automatically without manual intervention.

If the functionality for automatic switch-over between inputs is activated and in case the above-mentioned error appears the transmitter must switch from the input A (main signal) to the input B (backup signal). When the failure disappears the transmitter must, after an adjustable hysteresis (min. 10 min) switch back to input A. In case of failure on input B the transmitter must immediately switch to input A. A possible toggling between the two inputs must be prevented.

### Pre-correction

#### Manual pre-correction

If manual manual pre-correction methods for the correction of the non-linear and linear distortions are used, the corresponding pre-correction tables must be saved in the device. It must be possible to save at least two such tables:

- At nominal output power

- At -3 dB of nominal output power

Pre-correction tables must be stored in the device upon delivery. It must be possible to disable the pre-correction.

#### Adaptive pre-correction

If automatic linear and non-linear adaptive pre-correction is required, it must provide the following modes of automatic optimization of the transmitter performance:

- Single,

- Continuous,

- Monitoring.

Digital adaptive precorrection improves the modulation error ratio (MER) and shoulder attenuation.

Input level signal for adaptive precorrection must be in the 0 dBm +/- 5dB range.

### TPS

For possible alignment with other DVB-T/T2 transmitters in a SFN network the exciter must have the possibility to set the TPS length indicator and Cell identifier.

- When the Cell identifier is used, the TPS length indicator value must be hex 1f.

- When the Cell identifier is not used, the TPS length indicator value must be hex 17 and the Cell identifier value must be 0.

### MIP

The transmitter must control the transmission mode and all the modulation parameters based on the information from MIP. It must support all controls specified in the technical report ETSI TR 101191. There must be an option to disable this MIP instruction set recognition.

### Test Signal/PRBS

The exciter must be able to generate a PRBS test signal undependable from the input signal in accordance with the technical report ETSI TR 101290 Annex F.

## Tuner

The tuner's task is to extract the desired signal from the incoming high-frequency signal. The signal frequency must be adjustable in the range from 470 MHz to 862 MHz, or channels 21 to 69. The channel bandwidth is 8 MHz.

The tuner must fulfill all requirements for incoming signal levels from -70 to -37 dBm (transposer) and -70 to -20 dBm (repeater). The tuner must operate reliably also in the presence of strong adjacent channels, even if they are 30 dB above wanted signal level.

If the input signal falls below the set threshold, the output signal must be switched off. After the signal returns or the input signal level increases, the output signal must be switched on again. The hysteresis must be adjustable. In the event of fluctuations in the input signal level, the output power must be balanced to a value of 0,5 dB within 1 second. It must be possible to switch between automatic and manual gain adjustment.

## Mixer

The mixer transposes the COFDM signal from IF frequency to required RF output channel. Local oscillator, which is built in the mixer must meet the criteria for stability and accuracy. If an uninterruptible power supply is required, the mixer must be powered from it.

## Echo canceller

The task of the echo canceller is to remove self interference and static/dynamic echoes from the received signal.

The echo canceller must operate reliable even in presence of echoes with more than 10 dB over tuned signal level. It must be also possible to disable the echo canceller.

In case of presence of multiple echoes the output power may be temporary reduced to achieve stable operation. When the disturbance disappears, the device must automatically return to the required nominal output power.

## Working Frequency

### Frequency Range

The nominal center frequency is the signal middle frequency. The device must cover the UHF frequency band from 470 MHz to 862 MHz i.e. channels 21 to 69. Channel spacing is 8 MHz. The device must be easily tunable to any frequency inside the prescribed frequency band. The device must be adjustable in the range of 250 kHz in steps of 1 Hz.

### Exciter IF stage

If the direct modulation principle is not used, the intermediate frequency (IF) must be in the range of 35,5 to 36,6 MHz. The default value is 36 MHz. It must be possible to invert the IF spectrum.

## Synchronization

### Frequency and time reference

Table 1: Frequency and time reference

| Reference signal | Requirements |
| --- | --- |
| 10 MHz | Frequency accuracy < 1×10E-9 |
| 1 pps | Time Deviation < 250 ns |

### Stability

The center frequency must be synchronized to the internal 10 MHz reference signal. When it is not synchronized to the external reference signal the center frequency accuracy must be 10E-7 per year.

For the operation in a SFN network the transmitter must have built-in SFN synchronization unit. The transmitter must than meet the requirements for the frequency stability and timing in accordance with the technical specification ETSI TS 101191. The transmitter must evaluate the MIP information in the transport stream and accordingly set the transmission parameters. If the transmitter for whatever reason cannot meet the bit synchronization and the frequency synchronization, then the transmitter must be switched off immediately.

### Internal Reference

The source of internal reference is a built-in GPS receiver unit. The receiver must have additional reference output to feed additional transmitters with the reference signal. Output must have the same characteristics as valid for the external reference input.

In case of double drive configuration or 1+1 configuration the GPS receiver must be doubled in the way that each exciter has its own GPS receiver.

The implementation can also be with the external double GPS receiver and an automatic switching unit. In this case the switching unit must be connected to the transmitter in a way to transfer the GPS failure to the transmitter.

For the GPS antenna the following connector is required: 50 Ω, BNC/SMA, asymmetric.

### External Reference

The transmitter must have an external 10 MHz reference signal input. It must be able to synchronize to this external signal.

Specifications for reference signal input interface:

- Connector: 50 Ω, BNC/SMA, asymmetric

- Signal: sinusoidal or square

- Level: 0,5 to 2,5 Vrms

### Behavior In case of GPS Failure

When the GPS failure occurs the transmitter performance must not be impaired. When the GPS receiver is locked the local oscillator must be synchronized with GPS reference. The switching between locked and unlocked GPS receiver must not influence in the transmitter operation.

The transmitter must be automatically switched off when the requirements for the timing of dynamic delay compensation are not met. There must be a possibility to deactivate this functionality manually or remotely.

If the transmitter operates with a failed GPS receiver the transmitter must not reach the limit value sooner than in 12 hours.

The status of GPS receiver, the number of satellites and the signal level must be accessible by the control/management interface of the transmitter control unit and/or automatic switching unit.

### SFN Propagation Delay Compensation

The signal delay between the transmitter input (input transport stream) and the transmitter output because of signal processing inside the transmitter without any additional static or dynamic delay for the compensation of propagation and network optimization must be specified by the producer and must not exceed the value 50 ms.

### Dynamic Delay Compensation

The transmitter must have automatic dynamic signal propagation delay compensation, which allows compensation for the difference in delay on the signal path to the transmitter. This compensation must compensate for delays of up to 1 second. It must be able to compensate for the changing delay in the range of 250 us without interrupting the transport stream.

Synchronization point for the dynamic delay compensation is the transmitter output.

### Static Delay Compensation

For network optimization a transmitter must also have static delay compensation. This delay must be adjustable locally or remotely.

The delay must be adjustable in steps smaller than 150 ns up to the value of 10 ms in all modes of operation. This delay must be saved in memory and reloaded in case of power failure.

## Transmitter power

### Output power

Output power is the effective output power of a DVB-T/T2 that is measured at the output of a device by a thermal power measurement method.

If a transmitter with an output filter is required, the output power is measured after the output filter.

In case where the output filter is not required and is located in the channel combiner the measurement is performed on the monitoring terminal of channel combiner.

It must be possible to reduce the output power in steps of 0,1 dB up to -6 dB in reference to nominal power. By reducing the power all quality requirements must be fulfilled. It is allowed to change the non-linear pre-correction.

### Nominal power

Nominal power is maximum output power at which the device meets all the required technical quality criteria.

### Power consumption

The power required by the device to achieve nominal output power. This must include the power consumption of all sub-stages of the transmitter (output stage, cooling, M&C, …).

### Stability

The tolerance of output power must be less than 0,8 dB in the temperature range of +5 do +45 °C and 5% tolerance of mains voltage. This stability must be achieved at the latest 2 min. after switching it on.

### Return Loss

Output impedance of device must be 50 Ω. The device must operate up to VSWR 1,3 (18 dB). At VSWR up to 1,7 (12 dB) the output power may be reduced up to 6 dB. On even worse VSWR (< 13 dB) the output stage must switch off 3 tries. Short or open circuit on the output of the device must not damage the device.

### Efficiency

Efficiency is the ratio of nominal power to power consumption. Measurement report of output power and power consumption of individual sub-stages must be included in the documentation.

## Output stage

If a compact design of the transmitter is required, the PA unit and exciter must be integrated into a common housing.

If a modular design of the transmitter is required, in order to increase operational reliability, the final PA stage can contain multiple PA units.

A safe exchange of PA units during operation must be possible. During this time a reduction of output power is allowed. After replacement, the transmitter must meet all the required quality criteria.

Shutdown or failure of individual PA units may result in reduced output power, but not interruption of operation. The control system of the transmitter must recognize, log and indicate this event.

The device must be able to work continuously even if individual PA units fail. Regardless of this the cooling system must operate normally.

## Measurement/test points

The device must be equipped with test points with various signals. It must be possible to make measurements without influence on the operation of the transmitter.

### Transport stream

Test point on the exciter must allow control of the transport stream which is used for generation of current COFDM signal. Connector must be 75 Ω, BNC/SMA.

### RF test points

Following test points must be provided and must not be used for transmitter internal purposes:

- On output of the exciter (in configuration above 200 W).

- On each individual PA unit if multiple PA units are used.

- Test points for forward and reflected power between output stage and channel filter (in configuration above 200 W).

- If a transmitter with an output filter is required, test points for forward and reflected power must be located at the output of channel filter.

All test points must be implemented as directional couplers according to the specification:

- Output level: -10 do +10 dBm,

- Source impedance: 50 Ω.

The test point on the device output must fulfill:

- Precision: 0,15 dB,

- Directivity: 26 dB,

- Deviation of amplitude frequency response over individual DVB-T/T2 channels must be less than 0,05 dB/MHz. Measurement report of amplitude frequency response is part of transmitter documentation.

### Isolation points

In the modular design there must be freely accessible separation points between individual stages of the transmitter where two devices can be separated:

- Between exciter and output stage and

- Between output stage and output channel filter.

# Quality of operation

## Oscillator phase noise

Phase noise of all oscillators inside the device must fulfill the following phase noise mask with and without connected external frequency reference. Measurement reports of phase noise are part of transmitter documentation:

Table 2: Oscillator phase noise

| Relative frequency | Relative level |
| --- | --- |
| 10 Hz | ≤ -55 dBc/Hz |
| 100 Hz | ≤ -85 dBc/Hz |
| 1 kHz | ≤ -85 dBc/Hz |
| 10 kHz | ≤ -95 dBc/Hz |
| 100 kHz | ≤ -112 dBc/Hz |
| 1 MHz | ≤ -130 dBc/Hz |

Picture 7: Phase noise mask

Measured phase noise levels (dBc/Hz) for specific frequencies must be part of the transmitter documentation:

Table 3: Frequency deviations

| Operation mode | fa / kHz | fb / kHz | fc / kHz |
| --- | --- | --- | --- |
| 8k | ±1.1 | ±2.2 | ±3.4 |

All measurements of phase noise must be done according to technical specification ETSI TR 101290.

## Shoulder attenuation

Shoulder attenuation - measured on output stage before channel filter according to technical specification ETSI TR 101290 must be greater than 37 dB.

## Spectrum mask

If an output filter is required, the output signal at nominal output power must meet following requirements:

- Critical mask or

- Non-critical mask.

The measurement procedure must be according to guideline  and instruction .

## Spurious emissions

Emissions on frequencies outside the operating channel are unwanted and must not exceed limit values for spurious emissions in guideline 1 chapter 5.

## Crest factor

Voltage peaks at nominal output power must not exceed 13 dB above effective voltage. Crest factor must be specified for output stage with and without channel filter. The measurement duration must also be specified.

## Modulation error ratio / MER

Measurement report of a calibrated instrument of type R&S ETL is part of the device documentation.

### Transmitter

Modulation error ratio (MER) of the transmitter must be ≥ 34 dB, measured at the output of the transmitter.

### Transposer

Modulation error ratio (MER) of the transposer must be ≥ 32 dB at input signal level -55 dBm with MER 38 dB.

In general, at nominal input signal level -45 dBm, admissible deterioration of modulation error ratio (MER) between the input and output must be < 2 dB.

### Repeater

Modulation error ratio (MER) of the repeater must be:

- ≥ 32 dB at input signal level -50 dBm with MER 38 dB without the use of echo canceller,

- ≥ 26 dB at input signal level -50 dBm with MER 29 dB with present echo 5 dB higher than main received signal.

# Mains voltage

According to the device nominal power the connection to mains supply must be carried out in one or three phase. In case that nominal mains input voltage of 230 V / 400 V, 50 Hz vary in the range of +10% to -14%, the output power of the transmitter must not deviate by more than 10%. Power factor value: cos phi ≥ 0,95.

If a modular design of the transmitter is required, it must have separate power connections to the exciter , control unit and power amplifier(s). In case of a 1+1 configuration the switching unit must also be powered separately.

## Connection to the mains supply

If a modular design of the transmitter is required, it must be equipped with a main disconnect switch and automatic circuit breakers for individual units.

## Switch-on

The warm-up time after power-on or mains failure (> 1s) must not be longer than:

- 45 sec. in the multi frequency network (MFN),

- 45 sec. in the single frequency network (SFN) with use of reference signals (1pps, 10MHz),

- 10 min. in the single frequency network (SFN) with use of GPS receiver.

Within this time, deviations of the central frequency of at most ± 1*10-7 and deviations in timing conditions of up to 20% of the protection interval of the currently set operating mode may be present.

## Uninterruptible Power Supply

### Built-in power supply

If uninterruptible power supply is required it must ensure smooth operation of exciter, GPS receiver, control unit and change-over control unit.

Uninterruptible power supply must provide at least 20 minutes of autonomous operation.

States and events of uninterruptible power supply must be collected in the change-over control unit and/or device control unit and must be accessible through the user interface.

### External power supply

If configuration with external uninterruptible power supply is required device must allow connection of an external uninterruptible power source, which separately supplies exciter, GPS receiver, control unit and change-over control unit in case of 1+1 configuration.

The connection point for external uninterruptible power supply must be clearly marked and connection scheme must be attached to the documentation.

# Input band-pass filter

If the input band-pass filter is required, it must fulfill the following requirements:

- Implemented with least three LC circuits

- Must be tunable over the entire frequency band

- Pass band: 470 – 862 MHz

- Bandwidth: 9 MHz

- Pass band attenuation: < 1,5 dB

- Stop band attenuation: > 40 dB

- Return loss: > 18 dB

Filter can be mounted in several different ways:

- Inserted in the device

- Mounted on a carrier together with the output filter

- Mounted on a carrier for mounting in 19'' rack

# Output channel band-pass filter

If the output channel band-pass filter is required, the device must include filter with wiring cables and must be an integral part of the device. It must be adapted to the nominal power of the device and to the loads that occur during any power or voltage peaks. The filter must be tunable over the entire frequency band. A measurement log of the transmission characteristics of the operating channel in the range for the spurious, out-of-band transmission and harmonic waves (VSWR, amplitude and phase frequency response, typical temperature behavior) and tuning instructions must be provided.

# Dummy load

Transmitter in passive standby configuration (1+1) must contain a dummy load, which allows maintenance of the transmitter in reserve. The dummy load is connected into the system over RF switch.

Dummy load must be adapted to the nominal power of the transmitter.

# Cooling system

Cooling system of DVB-T/T2 devices can be performed with liquid or air cooling.

Heat dissipation into the room of the entire device with all its components must not exceed:

Table 4: Heat dissipation

| Volume of the device | Allowed dissipation |
| --- | --- |
| 0,5-2 m3 | 1,5 kW/m3 |
| 2-5 m3 | 1 kW/m3 |
| 5-10 m3 | 0,75 kW/m3 |

## Liquid Cooling

Liquid cooling must be carried out through two pumps. Each of those pumps must be able to provide necessary flow of coolant. Both pumps can work in change-over mode, so that one is always in reserve and full redundancy is achieved.

Piping between the cooling system and heat exchanger must be made from metal. It is allowed to use short piece of non-metallic pipe for vibration compensation. All piping must be carried out in such a way that in case of leakage water does not run on to device and its electrical components. The cooling system and the valves must be mounted inside the building and only heat exchanger must be mounted outside. When the device is not working, coolant must not freeze until the temperature of -45 ° C.

At maximum allowed outside permissible temperature of medium must not exceed 45 °C.

## Air Cooling

If air cooling with ducting is required, cooling must be carried out through a fan, which is installed inside the device. Heat dissipation from the device into the room must be as low as possible. Air ducting must be used for air intake and outlet. It must be possible to mount the air intake/outlet at the bottom or top of the device.

If stand-alone air cooling is required, cooling must be carried out through a build-in fan, which is installed inside the device and blows hot air into the surrounding area.

# Control and monitoring

Control and monitoring of device must be provided via an interface for local and remote control.

The control unit must contain built-in Linux operating system.

All device settings must be stored in the control unit and be protected against power failure. The device must be able to store two complete configurations including pre-correction settings.

In case of a false command the device must not be damaged.

Transmitter in passive standby configuration (1+1) must contain change-over control unit, which is responsible for controlling and change-over between main and spare transmitter.

Change-over control unit consists of control unit and RF switch. RF switch must be motor driven, bistable and must be adapted to the nominal power of the transmitter.

Change-over control unit must be implemented in that way that a failure in the RF switch does not cause a failure of transmitter, or other equipment.

Change-over control unit must support two modes:

- Manual - change-over control is not performing automatic switching between transmitters. Local or remote change-over between main and spare transmitter is possible.

- Automatic - in case of failure of active transmitter change-over between main and spare transmitter is made automatically. Local or remote change-over is still possible.

When change-over control unit is in automatic mode of operation there must be possibility to set »stay in shape« function. This function with adjustable time interval (10-30 days) automatically toggles between transmitters in case of 1+1 configuration or between exciters in case of double drive configuration. It must be possible to switch off this function.

When change-over control unit is in automatic mode of operation and local change-over is initiated, change-over control unit must switch to manual mode of operation.

In the automatic mode of operation change-over control unit must in case of a failure on the transmitter A change-over to the transmitter B and vice versa. Any fluctuation between transmitters must be prevented.

## Event log

The control unit of the device must record all events/warnings/alarms in an event log (Table 5).

States 1 & 2 show the messages for each event.

Table 5:.Event log

| Event Name | Tx | Tran | Rep | CCU | State 1 | State 2 | Error Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Forward Power Low |  |  |  |  | Start | End | low forward power (adjustable threshold) |
| Forward Power Fault |  |  |  |  | Start | End | loss of forward power |
| Reflected Power Fault |  |  |  |  | Start | End | high reflected power |
| High Temperature |  |  |  |  | Start | End | over-temperature |
| No ASI |  |  |  |  | Start | End | missing ASI signal |
| No RF input |  |  |  |  | Start | End | missing RF input signal |
| ASI Switchover |  |  |  |  | To A | To B | ASI signal switch-over |
| GPS Fault |  |  |  |  | Start | End | GPS reception fault |
| Sync Fault |  |  |  |  | Start | End | loss of reference signal (1pps, 10MHz) |
| MIP Fault |  |  |  |  | Start | End | MIP error |
| COFDM modulator Fault |  |  |  |  | Start | End | COFDM modulator fault |
| Control Unit Fault |  |  |  |  | Start | End | control unit fault |
| PA Module Fault |  |  |  |  | Start | End | power amplifier module fault |
| PreA Module Fault |  |  |  |  | Start | End | preamplifier module fault |
| PS Module Fault |  |  |  |  | Start | End | power supply module fault |
| Interlock Open |  |  |  |  | Start | End | open interlock loop |
| Cooling Fault |  |  |  |  | Start | End | cooling system fault |
| TxA Fault |  |  |  |  | Start | End | transmitter A fault |
| TxB Fault |  |  |  |  | Start | End | transmitter B fault |
| CCU Fault |  |  |  |  | Start | End | change-over fault |
| Automatic Changeover |  |  |  |  | To A | To B | automatic change-over |
| Manual Changeover |  |  |  |  | To A | To B | manual change-over |
| Manual/Automatic Mode |  |  |  |  | To M | To A | change-over between manual and automatic mode |
| Local/Remote Mode |  |  |  |  | To L | To R | change-over between local and remote mode |
| AC power Fault |  |  |  |  | Start | End | loss of mains input voltage (by individual phase) |
| UPS Fault |  |  |  |  | Start | End | uninterruptible power supply fault [1] |

Testing of all possible events is an integral part of the measurement protocol.

## Local interface

States stated in Table 6 must be shown on first page of a display device of local interface.

Table 6: Local interface

| States | Tx | Tran | Rep | CCU |
| --- | --- | --- | --- | --- |
| current forward power (after output filter) |  |  |  |  |
| current reflected power |  |  |  |  |
| device temperature |  |  |  |  |
| TS fault |  |  |  |  |
| MIP errors |  |  |  |  |
| interlock |  |  |  |  |
| state of the carrier muting |  |  |  |  |
| status of the transport stream inputs |  |  |  |  |
| status of the frequency and time synchronization |  |  |  |  |
| state of RF switch |  |  |  |  |
| change-over control mode (manual/auto) |  |  |  |  |
| local/remote mode |  |  |  |  |
| active transmitter |  |  |  |  |
| Alarms |  |  |  |  |
| low forward power (adjustable threshold) |  |  |  |  |
| high reflected power |  |  |  |  |
| cooling system fault |  |  |  |  |
| over-temperature |  |  |  |  |
| Control functions |  |  |  |  |
| device switch-on/switch-off |  |  |  |  |
| all device parameters |  |  |  |  |

Local interface must allow full management of the device.

Local interface must offer simple change-over between manual and automatic mode (not more than three button presses).

## Remote interface

### Web GUI

After login and password the main window must appear. At least parameters stated in Table 7 must be shown in the main window of web GUI.

### SNMP/MIB

At least states and values from Table 7 must be supported via the SNMP GET.

At least control commands from Table 7 must be supported via the SNMP SET.

SNMP/MIB interface must support SNMP TRAP functionality (Table 7). Traps must be sent automatically according to events described under Event log. When there is a transition from a bad state to a good state corresponding "all clear" trap must be sent.

Table 7: Remote interface

| Web GUI | Tx | Tran | Rep | CCU |
| --- | --- | --- | --- | --- |
| forward and reflected power level |  |  |  |  |
| device temperature |  |  |  |  |
| status of ASI/TSoIP inputs |  |  |  |  |
| RF input level |  |  |  |  |
| forward and reflected power level of both transmitters |  |  |  |  |
| state of RF switch |  |  |  |  |
| change-over manual/auto mode |  |  |  |  |
| local/remote mode |  |  |  |  |
| device location |  |  |  |  |
| device type |  |  |  |  |
| transmission parameters |  |  |  |  |
| echo canceler parameters |  |  |  |  |
| synchronization parameters |  |  |  |  |
| pre-correction settings and monitoring parameters (mer, shoulders) |  |  |  |  |
| output RF parameters |  |  |  |  |
| PA parameters (temperature, voltages, currents) * if compact design is used |  |  |  |  |
| external PA parameters (temperature, voltages, currents) * if modular design is used |  |  |  |  |
| power supply parameters |  |  |  |  |
| log of present faults – log of all alarms and warnings |  |  |  |  |
| SNMP/MIB (GET) |  |  |  |  |
| general alarm |  |  |  |  |
| states described under Event log |  |  |  |  |
| current forward power (after output filter) |  |  |  |  |
| current reflected power |  |  |  |  |
| device temperature |  |  |  |  |
| state of RF switch |  |  |  |  |
| SNMP/MIB (SET) |  |  |  |  |
| switch-on/switch-off |  |  |  |  |
| reset after a failure |  |  |  |  |
| transmitter switch-on/switch-off |  |  |  |  |
| change-over between transmitters |  |  |  |  |
| SNMP/MIB (TRAP) |  |  |  |  |
| states described under Event log |  |  |  |  |
| all clear |  |  |  |  |

IRT Technical Guideline - Requirement Profile for terrestrial DVB-T Transmitters 5/9 (October 2003)

Instruction of ARD - Messanweisung DVB-T Sender (January 2005)

Only in Double drive configuration