## Tabela minimalnih zahtev
ZŠ | zahteva | opis | zahtevano | Topic | Description | Required | Ponujeno | Referenca na dokument
1 | OSNOVNI PODATKI |  |  | MAIN DATA
2 | Maksimalna delovna moč sistema na točki priključitve | Sistem bo deklariran kot 40 MW vendar mora pri tem generirati tudi jalovo moč, da doseže cos fi = 0,8 | 40 MW @ cos fi = 0,8 | Maximun System Active power at POC | System will be declared as 40 MW but it shall generate also reactive power to reach P.F. = 0.8. | 40 MW @ cos fi = 0,8
3 | Minimalna instalirana moč sistema | Sistem mora zagotavljati dovolj jalove moči, da izpolnjuje zahteve iz RfG | 50 MVA | Minimal installed power of System | System shall provide enough reactive pover to fulfill RfG | 50 MVA
4 | Kapaciteta baterije | Bruto kapaciteta baterije po tovarniških preizkusih | 120 MWh + max 10% | Storage Capacity | Bruto capacity of battery after Factory Acceptance Test | 120 MWh + max 10%
5 | Izkoristek celotnega cikla | Izkoristek na točki priključitve (110 kV polje AE13). Upoštevati je potrebno izkoristke vseh naprav in povezav od 110 kV polja do baterije z upoštevanjem lastne rabe naprav in krmilnega sistema. | ≥ 81% | Round trip Efficiency | RTE at POC (HV bay AE13). All equipment from HV bay to the battery shall be considered including own consumption of the equipment and control system. | ≥ 81%
6 | Proizvajalci opreme na Tier 1 lestvici | Proizvajalec opreme mora biti uvrščen na Bloomberg NEF Tier 1 lestvico v zadnjih štirih celih kvartalih pred objavo razpisa. | da | Tier 1 list | The equipment manufacturer shall be included on the Bloomberg NEF Tier 1 list for the last four full quarters prior to the publication of the tender | Yes
7 | Izpolnjevanje zahtev iz Soglasja za priključitev (ELES) | Sistem mora izpolnjevati vse zahteve iz SONPO in RfG ter zahteve Agencije za Energijo. Izpolnjevati mora zahteve za tip D energetskega modula. | da | Compliance with requests from "Approval for Connection" (ELES) | The system must comply with all conditions from SONPO and RfG as well as the requirements of the Energy Agency. It complies with requirements for type D. | Yes
8 | BATERIJSKI SISTEM |  |  | BATTERY SYSTEM
9 | Tehnologija baterijskih celic | Zahteva se celice, ki imajo dobro razmerje med vzdržljivostjo, varnostjo in ceno. | LFP | Battery technology | The requirement is for cells offering an optimal balance of durability, safety, and cost. | LFP
10 | Dimenzije baterijskega kontejnerja | Zahteva se standardna dimenzija kontejnerja 20 ft. | da | Battery container dimensions | Standard 20 ft container is required. | Yes
11 | Kapaciteta kontejnerja | Bruto kapaciteta enega kontejnerja. | 5 - 6,5 MWh | Capacity of container | Bruto capacity of one container. | 5 - 6,5 MWh
12 | Življenjska doba | Število ciklov in pogoji pod katerimi to dosežemo. | ≥ 8000 ciklov | Lifetime | Lifetime Cycles and conditions to achieve this. | ≥ 8000 cycles
13 | Kapaciteta baterije po 1. letu | Pri obratovanju 1 cikel/dan pri 0.33C | ≥ 94 % | Capacity of the battery after 1 year | At operation of 1 cycle per day at 0.33C power. | ≥ 94 %
14 | Hlajenje baterij | Hlajenje baterijskih paketov | tekočinsko | Battery cooling system | Battery pack cooling | liquid
15 | KONVERTERSKI SISTEM (PCS s transformacijo) |  |  | INVERTER SYSTEM with transformer
16 | Način umestitve konverterjev | Umestitve konverterske opreme na skidu. Lahko skupaj s transformatorjem. | namestitev na 20 ali 40 ft okvirju / kontejnerju | Inverter installation | All inverter equipment and transformers shall be installed on a skid frame or container | installation on 20 or 40 ft skid frame or container
17 | HRUP |  |  | NOISE
18 | Emisije hrupa na merilnih/referenčnih točkah | Ponuditi izvedbo, ki ima čim nižji nivo hrupa | ≤ 45 dBA | Noise Emission at measurement / reference points | Offer a design with the lowest possible noise level. | ≤ 45 dBA
19 | SKUPNE ZAHTEVE |  |  | COMMON REQUIREMENTS
20 | Temperaturno območje delovanja | Temperaturno območje okolice pri kateri še ne pride do znižanja zmogljivosti. | -20 .. +40 °C | Temperature range | Ambient temperature range at which no performance derating occurs. | -20..+40 °C
21 | Black Start | Zahtevane lastnosti: - zagon brez zunanje napetosti - možnost vzpostavitve otoka - možnost dviga napetosti po rampi (mehki zagon) - otočno napajanje porabnikov - možnost sinhronizacije na omrežje (ročno spreminjanje f in U) - preklop v normalno delovanje (paralelno z mrežo) | da | Black Start | Required features: - Start-up without external voltage - Capability to establish an island mode - Ability to ramp up voltage (soft start) - Island supply for consumers - Capability for synchronization with the grid (manual adjustment of frequency and voltage) - Switch to normal operation (parallel with the grid) | Yes
22 | RfG Tip D analogija | Vključene vse zahteve iz Člena 16 RfG (razen izjem), ki veljajo za visoko napetost | da | RfG Type D analogy | Requirements from Article 16 (excluding the specific exemptions) that apply to high-voltage connections are included | Yes
23 | Grid-Forming (GFC) | Oprema je sposobna delovati kot napetostni vir (VSM) in zagotavljati sintetično vztrajnost. | da | Grid-Forming (GFC) | The equipment is capable of operating as a voltage source (Virtual Synchronous Machine - VSM) and providing synthetic inertia | Yes
24 | FRT (Premostitev napak) | Razsmerniki podpirajo neodvisno krmiljenje faz (negativno zaporedje) za nesimetrične okvare na 110 kV | da | Fault Ride Through (FRT) | The inverters support independent phase control (negative sequence current injection) for asymmetrical faults on the 110 kV grid | Yes
25 | Polna jalova moč tudi pri P = 0 W | Sistem omogoča polno jalovo moč tudi pri P = 0 W (STATCOM način) | da | Full reactive power at P = 0 W | The system allows full reactive power provision even at P = 0 W (acting in STATCOM mode) | Yes
26 | Obratovanje po izpadu omrežja | Sistem mora delovati tudi po izpadu omrežja. Če pride do izpada omrežja, pri čemer ostane VN odklopnik sklenjen, mora regulator preklopiti na otočno obratovanje. | da | Operation after Grid Rejection | System shall operate also after Grid Rejection. System shall switch to Island Mode Operation after Power Grid collapse if HV CB remains closed. | yes
27 | Izpad bremena | Sistem mora napajati lastno porabo, tudi če pride do izpada VN odklopnika. | da | Load Rejection | System shall be capable to supply own consumption in case of load rejection (HV CB opens). | Yes

## Tabela podatkov
ZŠ | zahteva | opis | zahtevano | Topic | Description | Required | Ponujeno | Referenca na dokument
1 | OSNOVNI PODATKI |  |  | MAIN DATA
2 | Rok dobave celotne opreme | Dobavi se BHEE, PCS, transformatorji, stikališče, nadzorni in krmilni sistem. | V skladu s Prilogo 2 Pogodbenega sporazuma | Lead time | Delivery of complete BESS, PCS, transformers, switchgear, control system | In accordance with Annex 2 of the Contract Agreement
3 | BATERIJSKI SISTEM |  |  | BATTERY SYSTEM
4 | Najmanjša baterijska enota | Kolikšna je najmanjša baterijska enota, ki se lahko menja na terenu? |  | Smallest Battery unit | What is smallest unit of battery system that can be raplaced on-site.
5 | Najmanjši izpad kapacitete | Kolikšen je izpad kapacitete, če pride do okvare ene baterijske celice? (odstotek ali delež celotne kapacitete kontejnerja) |  | Smallest Capacity loss | What is capacity loss if one battery cell fails? (percentage or a part of complete capacity of container)
6 | Območje uporabe | Kakšno je območje napolnjenosti baterije, ki zagotavlja normalno življenjsko dobo (cca 8000 ciklov) - minimalni in maksimalni SoC (npr. 4% - 95 %) |  | Depth of Discharge | Battery state-of-charge range that ensures normal service life (approx. 8,000 cycles) – minimum and maximum SoC (e.g., 4% – 95%)
7 | Čas mirovanja | Ali potrebuje baterija določen čas mirovanja preden se lahko zopet prazni: - trajanje? - pod kakšnimi pogoji ni potreben? |  | Rest time | Does battery need any rest time after charging before we can discharge it: - duration - under what conditions it is not needed
8 | Degradacija (SOH) | SoH po letih za obdobje 20 let obratovanja: - tabela "Degradacija" - opisati vpliv časa, tudi če ne obratuje: - pri SOC 100% - pri SOC 70 % - pri SOC 50 % |  | Degradation (also SOH at EOL) | State of Health (SoH) for each year in a 20-year operating period: - sheet "Degradation" - Describe the effect of time, even when not operating: - at SOC 100% - at SOC 70 % - at SOC 50 %
9 | Preostala kapaciteta baterije po 10 letih obratovanja | Pri obratovanju z 2 cikloma na dan, pri moči 0,33C in 100 % stopnji praznjenja | ≥ 70% | SoH after 10 years of operation | At operation with 2 cycles per day, 0.33C rate and 100% DoD | ≥ 70%
10 | Definicija cikla | Kako se šteje 1 cikel? Kako se šteje "žaganje" npr +/- 10 MWh @ <0.5C? (kot je npr. primarna/sekundarna reguacija) |  | Cycle definition | How is one cycle counted? How is ‘cycling’ counted, e.g., ±10 MWh at <0.5C? (as in primary/secondary regulation)”
11 | Ohišje baterijskega paketa | Iz kakšnega materiala je ohišje baterijskega paketa: - aluminijska pločevina - umetne mase … |  | Battery pack housing | What is the battery pack housing material: - aluminum sheet - plastic - …
12 | Zaščita baterijskega paketa | Kateri nivo IP zaščite ima posamezen paket? |  | Pack protection | What level of IP protection has battery pack?
13 | Sestava kontejnerja | - število celic v paketu - število paketov v regalu - število regalov v kontejnerju |  | Container assembly | - no. of cells in a pack - no. of packs in a rack - no. of racks in a container
14 | Nivo balansiranja bateriskega sistema | Na katerm nivoju se izvaja balansiranje (optimiranje)?: - celice med seboj - paketi med seboj - regali med seboj |  | Level of battery balansing (optimisation) | On which level battery system is balanced (optimized): - cells between each other - packs between each other - racks between each other
15 | Metoda balansiranja | Aktivno ali pasivno? |  | Balancing method | Active or pasive?
16 | Perioda balansiranja | Kako pogosto se izvaja balansiranje (optimiranje) sistema? Se izvaja ročno ali avtomatsko? Ali je potreben obisk serviserja? |  | Balancing period | How often balancing (optimizing) shall be performed? Is it performed avtomaticaly or manualy? Does it require attendance of service personel?
17 | KONVERTERSKI SISTEM (PCS s transformacijo) |  |  | INVERTER SYSTEM with transformer
18 | Vrsta konverterski sistema | String Inverter ali centralni (PCS) |  | Inverter type | String or Central inverter (PCS)
19 | Moč posameznega konverterja | Kolikšna je velikost konverterja, ki lahko izpade, medtem ko preostanek deluje nemoteno naprej? |  | Power of single inverter | What is the size of the inverter unit that can fail and the rest is operating normaly?
20 | Izhodna napetost konverterja | Kakšen je NN napetostni nivo? |  | Inverter output voltage | LV level
21 | Hlajenje konverterjev | Kakšno je hlajenje konverterjev? (tekočinsko hlajenje omogoča bolj učinkovito obvladovanje hrupa) | preferirano tekočinsko | Inverter cooling | Liquid cooling of inverters enables more effective noise control. | liquid prefered
22 | Maksimalna skočna obremenitev | Kakšna je dovoljena skočna obremenitev sistema oziroma konverterja? |  | Maksimum step load | Maksimum step load of PCS / system?
23 | Minimalna moč | Kakšna je minimalna moč na izhodu, pri kateri lahko sistem deluje? Za potrebe zagona iz teme mora biti vrednost 0 MW. | 0 MW | Minimal Power | Minimal power at output that PCS can still operate normally? It is 0 MW to fulfill requirements of Black Start. | 0 MW
24 | Moč transformatorja NN/SN | Moč, vezava, ali je tronavitni? |  | LV/MV Transformer power | Power, Connection, is it 3-winding transformer?
25 | Izvedba transformatorja | Zaradi hrupa se zahteva oljni transformator. Lahko je s konzervatorjem ali hermetično zaprt | oljni | Transformer type | An oil-filled transformer is required for low noise operation. The transformer may be equipped with a conservator or be hermetically sealed. | oil
26 | Oprema transformatorja | Katere zaščitne in ostale naprave ima transformator vgrajene? | - buchholz rele - termometer + senzor - oljekaz + kontakt - varnostni ventil (pressure relief) - preklopka (tap-changer) | Transformer equipment | Which protective and other devices are built into the transformer? | - Buchholz relay - Thermometer + sensor - Oil level indicator + contact - Safety valve (pressure relief) - Tap changer
27 | Napetost na SN nivoju | Izhodna napetost SN transformatorja | 21 kV | MV level | MV transformer output voltage | 21 kV
28 | Vezava brez zankanja | Ali je na voljo opcija, da se inverterski skid oz. transformator priključi direktno na SN stikališče, brez RMU (Ring Main Unit)? | da | Connection wihout RMU | Is there an option to connect skid or transformer directly to MV switchgear without RMU? | yes
29 | SF6 skladnost | Prepovedana uporaba SF6 v skladu z uredbo EU 2024/573 | da | SF6 compliance | The use of SF₆ is prohibited in accordance with EU Regulation 2024/573. | Yes
30 | HRUP |  |  | NOISE
31 | Diagram sevanja hrupa | Opisati vire hrupa in priložiti diagrame, ki omogočajo izdelavo modela oz. študije hrupa (baterijski kontejner, PCS skid…) | priložiti | Noise emission diagram | Describe the sources of noise and provide diagrams that enable the creation of a noise model or study (battery container, PCS skid…) | attach
32 | Dušenje hrupa | Ali imajo naprave možnost dodatnega dušenja hrupa (protihrupne rešetke, stene, …) |  | Noise reduction | Do the devices have the option for additional noise attenuation (soundproof grilles, walls, etc.)?
33 | SKUPNE ZAHTEVE |  |  | COMMON REQUIREMENTS
34 | Tloris | Izdelati tloris postavljene opreme na predlogo. Vključene naj bodo tudi vse potrebne kinete in cevne kanalizacije za polaganje energetskih in signalnih kablov. | priložiti | Layout | Prepare a layout of the installed equipment on the teplate. It should also include all necessary trenches and cable ducts for laying power and signal cables. | attach
35 | Round-trip izkoristek | Kolikšen je izkoristek sistema od polnjenja in shranjevanja do praznjenja baterije in ponovne pretvorbe v izmenično napetost na VN nivoju? | Izpolniti zavihek "Efficiency" | Round-trip efficiency | Specify the overall round-trip efficiency of the system, including charging, storage, discharge, and conversion back to AC at the HV level. | Fill data on sheet "Efficiency"
36 | Lastna raba sistema | Kakšna je lastna poraba sistema v mirovanju (kWh)? | Izpolniti tabelo "Own Consumption". | House-load of the system | What is the consumption in stand-by. | Fill table on sheet "Own Consumption".
37 | Enopolna shema | Enopolna shema shema iz karere je razvidno kako so različni moduli medsebojno povezani, kateri stikalni elementi so vključeni v dobavo, kakšni preseki kablov so potrebni | priložiti | Single line diagram | Single line diagram which shows how modules are connected, what switching equipment is included, what size of cables is needed. | attach
38 | RfG 2.0 Ready | Nadgradljivost programske opreme za skladnost z revidirano uredbo. | da | RfG 2.0 Ready | Required software/firmware upgradeability to ensure future compliance with the revised network code | Yes
39 | Black start rezerva | Sistem omogoča minimalno energijsko rezervo (SoC) za potrebe zagona brez zunanjega napajanja (nastavljivo od 5-30%) |  | Black Start reserve | Does system allow setting for minimal energy reserve for Black Start purposes (can be set 5-30%)
40 | UPS | Sistem mora vsebovati UPS, ki zagotavlja napajanje vse opreme, ki je potrebna za izvedbo zagona brez zunanjega napajanja. Ali sistem uporablja lokalne UPS ali centralnega za vse kontejnerje? | avtonomija min. 8h | UPS | System shall have UPS that ensures power supply for all equipment required for performing a Black Start. Does it use local UPS's or central for all containers? | min 8 hr. Autonomy
41 | POŽARNA VARNOST |  |  | FIRE SAFETY
42 | Detekcija požara oz. dima | Kateri sistemi za zaznavanje požara ali dima so vgrajeni? | vsaj za dim, temperaturo ter plina CO in H2 | Fire and smoke detection | Which fire or smoke detection systems are installed? | at least smoke, temperature, CO and H2 gases
43 | Krmilnik za gašenje | Krmilnik, ki aktivira primeren nivo gašenja - pri katerih pogojih se vklopijo posamezni zaščitni ukrepi: znižanje moči, vklop prezračevanja, dovajanje aerosola, vklop sprinkler… | da | Fire suppression controller | Controller that activates the appropriate level of extinguishing – under which conditions individual protective measures are triggered: power reduction, ventilation activation, aerosol discharge, sprinkler activation… | Yes
44 | Način dovajanja gasilnega sredstva | Kam se dovaja gasilno sredstvo? - na vrhu kontejnerja za celoten volumen kontejnerja - posamičen priključek na vsak baterijski paket - … |  | Fire extinguishing agent delivery | Where is the extinguishing agent delivered to? - top of the container for complete container - to each battery pack - …
45 | Količina gasilnega sredstva | Kolikšna je količina gasilnega sredstva v enem kontejnerju (aerosola, hladilne tekočine…)? |  | Amount of extinguishing agent | What amount of extinguishing agent is installed in a container (aerosol, cooling liquid…)?
46 | Protipožarna centrala | Protipožarna centrala mora imeti primerne izhode za navezavo na glavno centralo | izhod | Fire suppression control panel | The fire alarm control panel must have appropriate outputs for connection to the main control panel. | output
47 | Svetlobna indikacija | Možnost svetlobne indikacije na kontejnerju, ki ima aktivirano protipožarno zaščito. | Signalna luč vidna iz vseh strani oz. sponke za dodatno zunanjo luč | Light indication | Option for visual indication on the container that has activated fire protection. | Signal light visible from all sides or terminals for external indicator
48 | Zunanji sistem za gašenje | Dry-pipe sistem na zunanji strani kontejnerja z gasilskim priključkom ali prirobnico. | da | External Fire suppression system | The dry-pipe system connection on the outside of the container. | yes
49 | Ognjevarni kontejner | Upoštevati standarde UL 9540A | vsaj 60 minut | Fire resistant container | According to UL 9540A standard | at least 60 mins
50 | Zagotovitev varnega tlaka v kontejnerskem prostoru. Razbremenilna loputa | Ali ima izpust plinov iz kontejnerja v primeru povišanega tlaka usmerjen navzgor, da ne pride do poškodbe osebja, ki se lahko nahaja v bližini? | da | Pressure reilef hatch | Gas discharge from the container in case of increased pressure must be directed upwards to prevent injury to personnel who may be nearby.
51 | Zajem požarne vode | Ali ima kontejner na dnu urejen zajem hladilne vode, ki se dovaja preko sprinkler sistema? Ali ima urejeno drenažo na dnu kontejnerja? Ali ima priključek za odvajanje zbrane požarne vode? |  | Fire water collection | Does the container have a fire-water collection system at the bottom, for the water being supplied through the sprinkler system? The contaminated fire water is then routed through a connector and piping into a tank.
52 | MEHANSKE LASTNOSTI KONTEJNERJEV |  |  | MECHANICAL PROPERTIES OF CONTAINERS
53 | Protikorozijska zaščita | Med transportom so kontejnerji podvrženi slabšim pogojem kot je na lokaciji in se zato zahteva višja stopnja AKZ | vsaj C5 | Corrosion protection | During transport, the containers are exposed to harsher conditions than at the installation site, and therefore a higher level of corrosion protection is required. | at least C5
54 | Stopnja zaščite | Oprema je postavljena na prostem. Vdor prahu ni zaželen. | vsaj IP54 | Ingress protection | The equipment is installed outdoors. Dust ingress is undesirable. | at least IP54
55 | Barva kontejnerjev | Barve kontejnerjev morajo biti nevtralne (siva - RAL7035, bela...). Logotip kot opcija. | da | Container Color | The containers must be painted in neutral colors (gray – RAL7035, white...). Logo option available. | yes
56 | Oznake | Kontejnerji morajo imeti oznake za hitro identifikacijo v primeru požara, ki so vidne iz vseh smeri in berljive iz razdalje vsaj 30m. Oznake, ki se skladajo z načrti, morajo biti vsaj poleg nadzorne enote in morajo biti in berljive iz razdalje vsaj 3 m. | da | Labels | Containers must have markings for quick identification in case of fire, visible from all directions and readable from a distance of at least 30 m. Markings that correspond to the plans/drawings must be placed at least next to the control unit and must be readable from a distance of at least 3 m. | yes
57 | KOMUNIKACIJA |  |  | COMMUNICATION
58 | Kontrolni prikaz | Vsak modul (konverter, BMS…) mora imeti lokalni prikaz delovanja (display ali kontrolne lučke) s katerimi se hitro identificira napravo v okvari. | da | Local signalization | Each module (inverter, BMS, etc.) must have a local operation display (screen or indicator lights) that allows quick identification of a faulty device. | yes
59 | Komunikacijski protokoli proti zunanjemu EMS | IEC 61850 IEC 60870-5-101 IEC 60870-5-104 Modbus | da | Communication protocols available to external EMS | IEC 61850 IEC 60870-5-101 IEC 60870-5-104 Modbus | yes
60 | Kibernetska varnost | Komunikacija mora ustrezati standardu ISO 27001 in ostalim zahtevam v skladu z NIS2 oziroma ZINFV1 | da | Cyber Security | Communication must follow ISO 27001 requirements and requirements for critical infrastructure | yes
61 | Postaja za lokalno upravljanje in nadzor | Postaja za lokalno upravljanje in nadzor se nahaja v lokalnem komandnem prostoru, ki je v bližini baterijskih hranilnikov in inverterjev. Na njej se lahko izvaja monitoring, defektaža in tudi krmili sistem. | da | Local SCADA | The local control and monitoring station is located in a local control room near the battery storage units and inverters. It allows monitoring, troubleshooting, and system control. | yes
62 | Postaja za daljinsko upravljanje in nadzor | Postaja za daljinsko upravljanje in nadzor se nahaja v oddaljenem komandnem prostoru, ki je na lokaciji lastnika sistema. Na njej se lahko izvaja monitoring, defektaža in tudi krmili sistem. (postaja je v bistvu identična lokalni, le da je na drugi lokaciji in se ji lahko onemogoči izdajanje komand) | da | Remote SCADA | The remote control and monitoring station is located in a remote control room at the system owner's site. It allows monitoring, troubleshooting, and system control. (The station is essentially identical to the local one, except it is at a different location and can be restricted from issuing commands.) | yes
63 | Daljinsko vodenje hranilnika | Preko tega vmesnika lahko sistem sprejema daljinske komande za spremembo referenčne vrednosti in načina obratovanja, pošilja pa se stanja sistema: Moč, SOH, SOC, Status… Sprejem komand se lahko onemogoči iz postaje za daljinsko ali lokalno vodenje. Na razpolago morata biti vsaj dve liniji, ki ju lahko izbere operater. | da | Remote Control | Through this interface, the system can receive remote commands to change the reference value and operating mode, and it sends system statuses: Power, SOH, SOC, Status… Command reception can be disabled from either the remote or local control station. | yes
64 | Nadzorni sistem | Na nadzornem sistemu morajo biti na razpolago vsi podatki o stanju posameznih komponent baterijskega sistema (temperature, napetosti, tokovi, moči,...) ter alarmi in opozorila ob odstopanjih oziroma napakah v sistemu. Sistem mora beležiti vse alarme, komande in statuse. | da | Monitoring system | The monitoring system must provide all data on the status of individual components of the battery system (temperatures, voltages, currents, power, etc.), as well as alarms and warnings in case of deviations or system faults. The system must record all alarms, commands, and statuses | yes
65 | Obratovanje brez povezava v Cloud | Baterijski hranilnik mora delovati s polno funkcionalnostjo brez povezave na internet. Povezava v Cloud se lahko uporablja le za statistično obdelavo. V tem primeru mora biti strežnik v EU. | da | Operation without Cloud Connection | The battery storage system must operate with full functionality without an internet connection. Cloud connectivity may only be used for statistical processing. In this case, the server must be located in the EU. | yes
66 | MERILNI SISTEM |  |  | MEASURING & METERING SYSTEM
67 | Merilni sistem za potrebe obratovanja | Vrednosti se morajo prikazovati na postajah monitoringa in vodenja | da | Measuring system | Values are available on monitoring and SCADA systems | Yes
68 | Obračunski merilni sistem | Nameščeni števci se bodo uporabljali za obračun električne energije ter za dokazovanje učinkovitosti sistema. | števci razreda 0,2 | Metering system | Installed meters shall be used for electricity billing and for checking the system's efficiency. | 0.2 class meter
69 | STANDARDI |  |  | STANDARDS
70 | Testi pred transportom baterij | UN 38.3 | da | Transportation Testing Requirements | UN 38.3
71 | Varnost baterij v stacionarnih aplikacijah | UL 1973 | da | Safety standard for batteries in stationary applications | UL 1973
72 | Varnost celotnega sistema | UL 9540 | da | Safety standard for Battery Systems | UL 9540
73 | Testiranje širjenja termičnega uhajanja | UL 9540A | da | Test Method for Evaluating Thermal Runaway | UL 9540A
74 | Varnostne zahteve za litijeve baterije | IEC 62619:2022 | da | Requirements and tests for the safe operation of secondary lithium cells and batteries | IEC 62619:2022
75 | Varnostne zahteve za PCS | IEC 62477-1:2022 | da | Safety requirements for power electronic converter systems and equipment | IEC 62477-1:2022
76 | Varnostne zahteve za sekundarne litijeve celice | IEC 63056:2020 | da | Requirements and tests for the product safety of secondary lithium cells and batteries | IEC 63056:2020
77 | Minimalne zahteve za namestitev baterij | NFPA 855 | da | Installation of Stationary Energy Storage Systems | NFPA 855
78 | Zahteve za vse hranilnike | IEC62933 | da | Electrical energy storage | IEC62933
79 | Tehnične zahteve za priključitev na distribucijska omrežja | EN 50549-2 | da | Generating plants to be connected in parallel with distribution networks | EN 50549-2
80 | EMC kompatibilnost | IEC 61000-2-4:2024 | da | Electromagnetic compatibility (EMC) | IEC 61000-2-4:2024
81 | Zahteve za močnostne transformatorje | IEC 60076 | da | Power transformers | IEC 60076
82 | Visokonapetostne stikalne naprave in krmilno opremo | IEC 62271-212:2022 | da | High-voltage switchgear and controlgear | IEC 62271-212:2022
83 | Nizkonapetostne stikalne in krmilne razdelilne omare | IEC 61439 | da | Low-voltage switchgear and controlgear assemblies | IEC 61439
84 | NAVODILA |  |  | INSTRUCTIONS AND MANUALS
85 | Navodila za montažo | ENG/SLO |  | Installation instructions | ENG/SLO
86 | Navodila za commissioning | ENG/SLO |  | Commissioning instructions | ENG/SLO
87 | Navodila za uporabo | ENG/SLO |  | User's manual | ENG/SLO
88 | Navodila za vzdrževanje | ENG/SLO |  | Maintenance manual | ENG/SLO
89 | POPRODAJNA PODPORA |  |  | AFTERSALES SERVICE
90 | Oddaljenost servisa | Servisno osebje mora biti v dosegu cca 500 km: Milano, Muenchen, Dunaj, Budimpešta. Kader mora biti usposobljen za samostojno defektažo in odpravo napake. Večurno čakanje na odgovor principala ni dopustno. |  | Service center distance | Service personnel must be within approximately 500 km: Milan, Munich, Vienna, Budapest. The staff must be qualified to independently perform troubleshooting and fault repair. Several hours of waiting for a response from the principal is not acceptable.
91 | Rezervni deli | Seznam rezervnih delov, ki bodo na lokaciji objekta in seznam rezervnih delov, ki so dobavljivi v skladu z vzdrževalno pogodbo. Rezerni deli, ki potrebujejo redno kondiciranje (battary pack), se vključijo, le če je smiselno in izvedljivo. |  | Spare parts | Which spare parts will be kept at the site and which are available within a few hours/days? Spare parts that require regular conditioning (battery pack) should be included only if reasonable and feasible.
92 | Možnost dodajanja funkcionalnosti | Sistem mora biti hardversko in softversko modularen, da se lahko doda funkcija (regulacija) ali meritev, ki v začetku ni bila predvidena. |  | Ability to add funtions | The system hardware- and software shall be modular so that a function (control/regulation) or a measurement that was not initially planned can be added later?
93 | Nadgradnje in posodobitve | Kako pogosto se izvaja pregled sistema s strani proizvajalca pooblaščene osebe? npr. 2x letno na lokaciji |  | Upgrade and update | How often is the system inspected by the manufacturer's authorized person? e.g. 2 times a year on-site
94 | GARANCIJE IN VZDRŽEVANJE |  |  | MAINTENANCE
95 | Splošna garancija | Splošna garancija na opremo in celotno izvedbo projekta - 3 leta |  | General warranty | General warranty on equipment and entire project implementation - 3 years
96 | Garancija in vzdrževanje sistema BHEE | Garancije na degradacijo, vzdrževanje sistema za 10 let (splošna garancija 3 leta + podaljšana garancija 7 let) | 10 let | System warranty and maintenance | Degradation warranties, system maintenance for 10 years (general warranty 3 years + extended warranty 7 years) | 10 years
97 | Garancija za razpoložljivost | planirano vzdrževanje se ne šteje v nerazpoložljivost | 97% | Availability warranty | planned maintennance does not count as unavailability | 97%
98 | Vzdrževalna pogodba | Priložite osnutek vzdrževalne pogodbe. Pred oddajo končne ponudbe bo naročnik bistvene točke vzdrževalne pogodbe enakopravno in tranparentno upošteval in vklučil v pogodbo. |  | Maintenance Contract | Attach a draft maintenance contract. Before submitting the final offer, the client will equally and transparently consider and include the essential points of the maintenance contract in the contract.

## Degradation
Operating condition [cycle/day] | DOD [%] | C-rate [P] | Temperature | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
0.5 | 100 | 0.25 | 25℃ | 0: 100%
1 | 100 | 0.25 | 25℃ | 0: 100%
1 | 95 | 0.25 | 25℃ | 0: 100%
1 | 90 | 0.25 | 25℃ | 0: 100%
1.5 | 100 | 0.25 | 25℃ | 0: 100%
1.5 | 95 | 0.25 | 25℃ | 0: 100%
1.5 | 90 | 0.25 | 25℃ | 0: 100%
2 | 100 | 0.25 | 25℃ | 0: 100%
2 | 95 | 0.25 | 25℃ | 0: 100%
2 | 90 | 0.25 | 25℃ | 0: 100%
0.5 | 100 | 0.5 | 25℃ | 0: 100%
1 | 100 | 0.5 | 25℃ | 0: 100%
1 | 95 | 0.5 | 25℃ | 0: 100%
1 | 90 | 0.5 | 25℃ | 0: 100%
1.5 | 100 | 0.5 | 25℃ | 0: 100%
1.5 | 95 | 0.5 | 25℃ | 0: 100%
1.5 | 90 | 0.5 | 25℃ | 0: 100%
2 | 100 | 0.5 | 25℃ | 0: 100%
2 | 95 | 0.5 | 25℃ | 0: 100%
2 | 90 | 0.5 | 25℃ | 0: 100%
0.5 | 100 | 0.33 | 25℃ | 0: 100%
1 | 100 | 0.33 | 25℃ | 0: 100%
1 | 95 | 0.33 | 25℃ | 0: 100%
1 | 90 | 0.33 | 25℃ | 0: 100%
1.5 | 100 | 0.33 | 25℃ | 0: 100%
1.5 | 95 | 0.33 | 25℃ | 0: 100%
1.5 | 90 | 0.33 | 25℃ | 0: 100%
2 | 100 | 0.33 | 25℃ | 0: 100%
2 | 95 | 0.33 | 25℃ | 0: 100%
2 | 90 | 0.33 | 25℃ | 0: 100%

## Efficiency
|  | Single system efficiency | [8 empty] | Whole train Efficiency
| 0.25C (40MW/120MWh) @25°C | Battery | HVAC & DC Self-loss | DC-PCS Cable | PCS | PCS-MCCB | MV Transformer | MV cables | MV Switchgear | HV Transformer | Accumulated Efficiency
Charging | Single trip efficiency including internal consumption | [9 empty] | 0%
Discharging | Single trip efficiency including internal consumption | [9 empty] | 0%
| 0.5C (40MW/120MWh) @25°C | Battery | HVAC & DC Self-loss | DC-PCS Cable | PCS | PCS-MCCB | MV Transformer | MV cables | MV Switchgear | HV Transformer | Accumulated Efficiency
Charging | Single trip efficiency including internal consumption | [9 empty] | 0%
Discharging | Single trip efficiency including internal consumption | [9 empty] | 0%
| 0.33C (40MW/120MWh) @25°C | Battery | HVAC & DC Self-loss | DC-PCS Cable | PCS | PCS-MCCB | MV Transformer | MV cables | MV Switchgear | HV Transformer | Accumulated Efficiency
Charging | Single trip efficiency including internal consumption | [9 empty] | 0%
Discharging | Single trip efficiency including internal consumption | [9 empty] | 0%

## Own Consumption
| Ambient temperature [°C] | Full Load [kW] | 50 % [kW] | Idle [kW]
Battery container aux power | -5
(HVAC,…) | 10
25
30
PCS skid aux power | -5
(Fans, Heaters,…) | 10
25
30
MV transformer | -5
(if not included in skid) | 10
25
30
MV switchgear | -5
10
25
30
HV transformer | -5
10
25
30
What is the power of the Auxiliary supply depending on load and ambient temperature.

## Arbitrage Data
Moč polnjenja |  | Charging Power | Pc | 40 | MW
Moč praznjenja |  | Discharging Power | Pd | 40 | MW
Kapaciteta baterije pri FAT |  | Battery Capacity at FAT | Capacity |  | MWh | minimum
Izkoristek pri polnjenju |  | Charge Efficiency | Efc |  | % | minimum
Izkoristek pri praznjenju |  | Discharge Efficiency | Efd |  | % | minimum
Zunanja temperatura |  | Ambient Temperature | Amb. Temp. | 25 | °C
Način obratovanja |  | Operation Regime | Regime | 2 | Cycles/day
Leto |  | Year | Year | SAT | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Povprečno stanje baterije | % | Average SoH | SoH avg.
Dejanska kapaciteta SoH | MWh | Actual Capacity SoH | Cap act.
Dejanske ure obratovanja | h | Actual operating hours | OH act.
Energija za polnjenje na 110 kV | MWh | Energy for Charging | Ec
Energija praznjenja na 110 kV | MWh | Energy at Discharging | Ed
Dejanske ure mirovanja | h | Actual Stand-by hours | SB act.
Energija lastne rabe na 110 kV | MWh | Energy for Own Consumption | Eoc
- Zapišite podatke za vsako leto posebej.
- Upoštevajte dejansko kapaciteto hranilnika SoH glede na degradacijo.
- Dejanske ure obratovanje tudi prilagodite SoH (manjša kapaciteta - krajši čas obratovanja pri polni moči).
- Upoštevajte tudi vse izgube pretvorb in prenosa od baterije do 110 kV polja.
- Upoštevati je potrebno tudi lastno porabo sistema med obratovanjem (če že ni vključeno v izkoristku) in v mirovanju (dejanske ure, ko se baterija ne polni oz. prazni).
Vhodni podatki:
Hranilnik deluje z nazivno močjo 40 MW.
Obratuje se 2 cikla na dan.
Uporabna kapaciteta baterije ob FAT je vsaj 120 MWh.
Izračun detajlno pojasnite in podajte vse uporabljene podatke.
- Record the data for each year separately.
- Take into account the actual storage capacity (SoH) regarding degradation.
- Adjust the actual operating hours to the SoH (lower capacity - shorter operating time at full power).
- Also take into account all conversion and transmission losses from the battery to the 110 kV bay.
- The system's own consumption must also be considered during operation (if not already included in the efficiency) and during standby (actual hours when the battery is not charging or discharging).
Input data:
The storage system operates with a nominal power of 40 MW.
It operates 2 cycles per day.
The usable capacity of the battery at FAT is at least 120 MWh.
Explain the calculation in detail and provide all the data used.