|  | Draft Purchase Order NO: |  |
| --- | --- | --- |

| Requisition: 8260843 |  |  |
| --- | --- | --- |
| RFQ No: 192101 |  |  |
| Your Reference: |  |  |
| PO Currency: |  |  |
| BILL TO: NPP Krško VRBINA 12 8270 KRŠKO SLOVENIA | SUPPLIER | _______________________ _______________________ _______________________ _______________________ _______________________ |
| SHIP TO: NPP Krško VRBINA 12 8270 KRŠKO SLOVENIA | END USER | NPP Krško d.o.o. VRBINA 12 8270 KRŠKO SLOVENIA sonja.zivic@nek.si Attn. of Sonja Živič |
| DATE: |  |  |
| PAGES: 8 |  |  |

Based on above references we are hereby placing our Purchase Order for the following: 1. SCOPE OF SERVICES Line; NEK Item Number; Part Number; Delivery Date; UOM; Quantity; Unit Price; Amount; Safety Classification. 1; 434529*; W16-0CP02-KBDNE*; 27-Mar-27; EA; 2,00; SR. VALVE.BUTTERFLY,SC:SR,TYPE:WAFER,SIZE:10",BODY MAT'L:SA105,ANSI RATING:150,ASME CODE CLASS:3,ACTUATOR:GEAR OPERATOR HBC-1. MFG: VELAN INC, BEEKMANTOWN ROAD, 12901 PLATTSBURGH, United States Item shall be supplied in accordance with the following TQRs: A00, A03, A07, B00, B01, B04, B06, B07, B08, F00, F02, F50, F51, F52, F521, F53, F55, F56, F57, F59, F60, F90, G00, G01, G03 The following documents and/or records shall be submitted with the above item: G05 - CERTIFICATE OF COMPLIANCE WITH PURCHASE ORDER REQUIREMENTS G09 - ASME QUALITY SYSTEM CERTIFICATES G22 - NONCONFORMANCE REPORTS G31 - STATEMENT OF CODE (ASME-II OR III) RECONCILIATION (IF REQUIRED) G33 - ULTRASONIC (UT) TEST RECORD G36 - LIQUID PENETRANT (LP) TEST RECORD OR REPORT G48 - HYDRO PRESSURE TEST RECORD G49 - LEAKAGE TEST RECORD G54 - HEAT TREATMENT RECORDS OR REPORTS G55 - CERTIFIED MATERIAL TEST RECORDS-MECHANICAL PROPERTIES G56 - CERTIFIED MATERIAL TEST RECORDS-CHEMICAL COMPOSITION G60 - ASME CODE MANUFACTURER'S DATA REPORT G622 - VALVE ASSEMBLY DRAWING G64 - OPERATION & MAINTENANCE MANUAL (2 COPIES) G67 - MANUFACTURING AND QC INSPECTION PLAN G69 - FINAL INSPECTION REPORT (VISUAL, DIMENSIONAL) G83 - DESIGN / STRESS REPORT G84 - SEISMIC ANALYSIS REPORT X002 - CERTIFICATE OF COMPLIANCE WITH TECHNICAL SPECIFICATION X04 - ASME CODE REQUIREMENTS X13 -INSPECTION WITNESS / HOLD POINT NOTIFICATION X19 - ADDITIONAL NOTES.

*Note: The Seller shall supply the above-stated or equivalent item in terms of required parameters and TQR requirements.

2. ANTI-CORRUPTION CLAUSE The contracting Parties Supplier and Purchaser shall undertake not to give, promise or receive any present or payment in cash or in any other valuable object to or from each other either directly or indirectly or through any official, officer or any other individual employed in the government or any authority (division, department, agency) or through any political party or any candidate of any political party with the intention of bribing so that any official, officer or any other employee, party or candidate would be tempted to abuse his/her position or to exert influence on any law or any decision made by government or any other competent government department with the purpose to obtain or retain a deal or to direct a deal to a commission agent or to any of his assistants, representatives, distributors, subsidiary companies or any other associated companies. In case the act stated in the previous paragraph has been committed or attempted to be committed, the Purchase Order that had been concluded or had come into force already shall become null and void. In case the Purchase Order is not valid yet, it shall be deemed not to be concluded.

3. TECHNICAL AND QUALITY REQUIREMENTS

A00 - GENERAL REQUIREMENTS ALL REQUIRED DOCUMENTS SHALL BE SUPPLIED IN ENGLISH OR ENGLISH/ MULTILINGUAL. A03 - ORDER ENTRY/DROP SHIP REQUIREMENTS THE SALES OFFICE RECEIVING THIS PURCHASE ORDER SHALL TRANSMIT ALL NEK PURCHASE ORDER REQUIREMENTS TO THE EQUIPMENT/ ITEM MANUFACTURER. ALL ITEMS SHALL BE DROP SHIPPED DIRECTLY FROM THE MANUFACTURER TO THE NEK FACILITY SPECIFIED ON THE PURCHASE ORDER.. A07 - NEW ITEMS ALL ITEM(S) PROVIDED ON THIS PURCHASE ORDER SHALL BE SUPPLIED IN THE NEW CONDITION (NOT USED OR REFURBISHED IN ANY WAY)....

B00 - QUALITY ASSURANCE REQUIREMENTS B01 - QUALITY ASSURANCE PROGRAM ALL SERVICES AND ITEMS, INCLUDING THOSE WHICH HAVE TO COMPLY WITH ASME CODE REQUIREMENTS, SHALL BE SUPPLIED IN ACCORDANCE WITH A QUALITY ASSURANCE PROGRAM THAT COMPLIES WITH 10CFR50 APPENDIX B AND ANSI N45.2-1977 OR ASME NQA-1, AND THAT HAS BEEN PREVIOUSLY EVALUATED AND ACCEPTED BY NEK.. B04 - SUPPLIER QA MANUAL CONTROLLED DISTRIBUTION IF A CONTROLLED COPY OF THE LATEST REVISION OF THE SUPPLIER'S QUALITY ASSURANCE PROGRAM MANUAL HAS NOT BEEN PREVIOUSLY SENT TO NEK, SUBMIT A COPY OF THIS DOCUMENT TO: LUKA MIKELIĆ, QUALITY & NUCLEAR OVERSIGHT DIRECTOR tel.:++386 748 02 429 E-mail:luka.mikelic@nek.si IF A REVISION TO THE SUPPLIER'S QUALITY ASSURANCE MANUAL IS MADE DURING THE CONDUCT OF WORK ASSOCIATED WITH THIS ORDER, A COPY OF THE REVISION SHALL BE SUBMITTED TO THE ABOVE ADDRESS PRIOR TO IMPLEMENTATION OF THE CHANGE.. B06 - 10CFR21 REPORTING THIS ORDER IS SUBJECT THE PROVISIONS OF THE TITLE 10 OF THE U.S. CODE OF FEDERAL REGULATIONS PART 21, REPORTING OF DEFECTS AND NONCOMPLIANCE, REPORTING PURSUANT TO 10CFR21 SHALL BE MADE TO: STANKO MANOJLOVIC , ENGINEERING SUPPORT FOR LONG TERM OPERATION SUPERINTENDENT tel:++386 748 02 527 E-MAIL: stanko.manojlovic@nek.si. B07 - RIGHTS OF ACCESS NUCLEAR POWER PLANT KRSKO (NEK)) SHALL HAVE THE RIGHT OF ACCESS TO THE SUPPLIER'S AND ANY SUBTIER SUPPLIER'S FACILITIES AND RECORDS FOR INSPECTION OR AUDIT BY NEK , THEIR DESIGNATED REPRESENTATIVE AND/OR OTHER PARTIES AUTHORIZED BY NEK. THIS SHALL INCLUDE, BUT IS NOT LIMITED TO, THE RIGHT TO AUDIT MATERIAL, TEST, INSPECTION SERVICES AND QUALITY RECORDS; MAKE SURVEILLANCE VISITS DURING MANUFACTURING; AND WITNESS TESTS TO THE EXTENT NEK DEEMS NECESSARY TO ASSURE THAT WORK IS BEING PERFORMED IN ACCORDANCE WITH ALL PRODUCT DESIGN AND MANUFACTURING REQUIREMENTS. NEK WILL MAKE ARRANGMENT FOR ANY SUBTIER AUDIT OR INSPECTION THROUGH SUPPLIER. SUPPLIER WILL HAVE OPTION TO ACCOMPANY NEK DURING ANY SUB-SUPPLIER AUDITS OR INSPECTIONS. INSPECTIONS OR EXAMINATIONS PERFORMED BY NEK, OR ITS DESIGNATED REPRESENTATIVES, DO NOT RELIEVE THE SUPPLIER OF ITS RESPONSIBILITY TO MEET THE REQUIREMENTS OF THIS PURCHASE ORDER.. B08 - RETENTION OF RECORDS A RECORD SYSTEM (RETENTION TIME FOR LIFETIME AND NON-PERMANENT RECORDS) SHALL BE ESTABLISHED AND MAINTAINED BY THE SUPPLIER THAT PROVIDES DOCUMENTARY EVIDENCE OF THE QUALITY OF THE ITEMS AND ACTIVITIES AFFECTING QUALITY. THESE QA RECORDS SHALL INCLUDE RESULTS OF REVIEWS, INSPECTIONS,TESTS, AUDITS, MONITORING OF WORK PERFORMANCE AND MATERIAL ANALYSIS. RECORDS SHALL, AS A MINIMUM, IDENTIFY THE INSPECTOR OR DATA RECORDER, DATE INSPECTION WAS PERFORMED, TYPE OF OBSERVATION, PROCEDURES USED, RESULTS, ACCEPTABILITY, AND ACTION TAKEN FOR DEFICIENCIES NOTED. ADDITIONAL RECORDS OF SUPPORTING DATA SHALL ALSO BE MAINTAINED. ALL QUALITY VERIFICATION RECORDS, PROCEDURES AND QUALIFICATIONS SHALL BE IDENTIFIABLE TO THE ITEM OR ACTIVITY INVOLVED. THESE RECORDS SHALL BE RETRIVEABLE AND AVAILABLE FOR EXAMINATION. THE CLASSIFICATION AND RETENTION TIME OF LIFETIME AND NON-PERMANENT RECORDS SHALL BE IN COMPLIANCE WITH THE REQUIREMENTS OF USNRC REGULATORY GUIDE 1.28, REV. 3-1985. THE SUPPLIER MAY DISPOSE OF NON-PERMANENT RECORDS AFTER THE REQUIRED RETENTION PERIOD. IF THE SUPPLIER GOES OUT OF BUSINESS BEFORE THE END OF THE RETENTION PERIOD OF THESE RECORDS, THE SUPPLIER WILL SEND ONE COPY OF THESE RECORDS TO THE NEK IMPORT DEPARTMENT SUPERINTENDENT....

F00 - SHIPPING, HANDLING, MARKING AND STORAGE INSTRUCTIONS ; F02 - HANDLING, PACKAGING AND SHIPPING HANDLING, PACKAGING AND SHIPPING OF THE ITEM SUPPLIED UNDER THIS PURCHASE ORDER SHALL BE IN ACCORDANCE WITH AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI) N45.2.2-LEVEL B.. F50 - ITEM MARKING REQUIREMENTS ALL ITEMS ARE TO BE PACKAGED INDIVIDUALLY AND IDENTIFIED WITH THE SPECIFIC PART NUMBER, OR ALL ITEMS OF A GIVEN PART NUMBER TO BE PACKAGED TOGETHER AND IDENTIFIED WITH THE SPECIFIC PART NUMBER AND THE FOLLOWING:. F51 - THE PURCHASE ORDER NUMBER. F52 - NEK ITEM NUMBER. F521 - PART/ CATALOG NO.. F53 - ASME CODE STAMP. F55 - HEAT NO. BATCH NO. OR CODE. F56 - RATING. F57 - MANUFACTURER'S NAME. F59 - ITEM SERIAL NUMBER. F60 - MATERIAL DESCRIPTION OR COMPOSITION. F90 - PACKING SLIPS ARE TO BE SHIPPED WITH ORDER...

G00 - SUPPLIER DOCUMENTATION REQUIREMENTS ALL REQUIRED DOCUMENTS SHALL BE SUPPLIED IN ORIGINAL HARD COPY OR ELECTRONIC FORM DEFINED BY SUPPLIER QA PROGRAM AND ACCEPTED BY NEK. G01 - DOCUMENT TRACEABILITY ALL REQUIRED DOCUMENTS SHALL BE TRACEABLE TO THE NEK PURCHASE ORDER. DOCUMENTS SUPPLIED WHICH ARE ASSOCIATED WITH SPECIFIC ITEMS ON THE ORDER, SUCH AS TEST REPORTS, SHALL BE IDENTIFIED IN ORDER TO ESTABLISH TRACEABILITY TO THAT ITEM OR GROUP OF ITEMS.. G03 - DOCUMENTATION DIRECTED ADDRESS DOCUMENTS SUBMITTED PRIOR TO SHIPMENT OR SUBSEQUENT TO SHIPMENT INCLUDING REVISIONS OF THESE DOCUMENTS, SHALL BE DIRECTED TO THE PURCHASING DEPARTMENT. EVERY PAGE OF EACH DOCUMENT SHALL BE TRACEABLE TO THE NEK'S PURCHASE ORDER AND APPLICABLE ITEM(S) NUMBER.. G05 - CERTIFICATE OF COMPLIANCE WITH PURCHASE ORDER REQUIREMENTS THE CERTIFICATE OF COMPLIANCE SHALL SATISFY THE FOLLOWING CRITERIA: 1. IDENTIFY THE PURCHASE ORDER NUMBER, INCLUDING ITEM NUMBERS AND CHANGE ORDER NUMBER APPLICABLE TO THE ITEM BEING CERTIFIED. 2. A PERSON IDENTIFIED IN THE SUPPLIER'S QUALITY ASSURANCE PROGRAM DESCRIPTION AS RESPONSIBLE FOR CERTIFICATION SHALL ATTEST TO THE CERTIFICATE BY SIGNATURE, TITLE AND DATE OF SIGNING. 3. SUPPORTING DOCUMENTATION TO SUBSTANTIATE THE CERTIFICATE SHALL BE INCLUDED, UNLESS OTHERWISE WAIVED BY NEK. 4. NEK RESERVES THE RIGHT TO DETERMINE THE VALIDITY OF THE CERTIFICATE OF COMPLIANCE BY AN AUDIT OF THE SUPPLIER OR BY AN INSPECTION OR TEST OF THE ITEM(S).. G09 - ASME QUALITY SYSTEM CERTIFICATES MATERIAL SHALL BE SUPPLIED IN ACCORDANCE WITH ASME SECTION II AND/OR III UNDER AN APPROVED NCA-3300/4200 PROGRAM BY A MATERIAL ORGANIZATION (MO) OR APPROVED SUPPLIER HAVING AN ASME QUALITY SYSTEM CERTIFICATE. MATERIAL ORGANIZATION OR APPROVED SUPPLIER SHALL INCLUDE HIS CERTIFICATE NUMBER AND EXPIRATION DATE ON THE 'CMTR' OR CERTIFICATE OF COMPLIANCE AS REQUIRED BY 'ASME'.. G22 - NONCONFORMANCE REPORTS THE SUPPLIER SHALL PROVIDE A COPY OF ALL NONCONFORMANCE REPORTS AS REPAIR OR USE-AS-IS DISPOSITION OF MATERIALS DURING THE MANUFACTURING PROCESS TO UTILITIES ONLY IN CASES THAT AFFECT ENVIRONMENTAL QUALIFICATION, INTERCHANGEABILITY, DESIGN OR OPERATING PARAMETERS GENERATED DURING MANUFACTURE OF PROCESSING OF THIS ORDER. THIS REPORT SHALL INCLUDE TECHNICAL JUSTIFICATION FOR NONCONFORMANCE DISPOSITIONS. ALL DISPOSITIONS WHICH DO NOT RETURN AN ITEM TO THE CONDITIONS STATED IN AN APPROVED DRAWING OR SPECIFICATION SHALL BE APPROVED BY NEK PRIOR TO THE SHIPMENT OF THE AFFECTED ITEM.. G31 - STATEMENT OF CODE (ASME-II OR III) RECONCILIATION (IF REQUIRED) THE RECONCILIATION REPORT TO THE ORIGINAL CODE EDITION AND ADDENDA IS REQUESTED TO BE SUBMITTED FOR REVIEW PRIOR TO MACHINING OF PART. COMPONENT/ PART SHALL MEET THE LATEST ASME CODE EDITION AND ADDENDA APPROVED BY NRC NUCLEAR REGULATORY COMMISSION) AS STATED IN 10 CFR 50.55A.. G33 - ULTRASONIC (UT) TEST RECORD. G36 - LIQUID PENETRANT (LP) TEST RECORD OR REPORT. G48 - HYDRO PRESSURE TEST RECORD. G49 - LEAKAGE TEST RECORD. G54 - HEAT TREATMENT RECORDS OR REPORTS. G55 - CERTIFIED MATERIAL TEST RECORDS-MECHANICAL PROPERTIES. G56 - CERTIFIED MATERIAL TEST RECORDS-CHEMICAL COMPOSITION. G60 - ASME CODE MANUFACTURER'S DATA REPORT. G622 - VALVE ASSEMBLY DRAWING. G64 - OPERATION & MAINTENANCE MANUAL (2 COPIES) THE DOCUMENT SHOULD INCLUDE THE FOLLOWING NPP KRŠKO SPECIFIC DATA: NPP KRŠKO PURCHASE ORDER NUMBER, NPP KRŠKO TECH.(EQUIPM.)SPEC. NUMBER, EQUIPMENT ID (TAG)NUMBER.. G67 - MANUFACTURING AND QC INSPECTION PLAN THE SUPPLIER SHALL PROVIDE THE ITEM MANUFACTURING ACTIVITIES AND QC INSPECTION PLAN TO NPP KRŠKO FOR THE REVIEW AND DEFINITION OF NPP KRŠKO QC WITNESS / HOLD POINTS. QC INSPECTION PLAN SHALL BE SUBMITTED TO NEK AT LEAST 14 DAYS PRIOR TO START OF MANUFACTURING.. G69 - FINAL INSPECTION REPORT (VISUAL, DIMENSIONAL). G83 - DESIGN / STRESS REPORT THE DOCUMENT SHOULD INCLUDE THE FOLLOWING NEK SPECIFIC DATA: NPP KRŠKO PURCHASE ORDER NUMBER, NPP KRŠKO TECH.(EQUIPM.)SPEC. NUMBER, EQUIPMENT ID (TAG)NUMBER.. G84 - SEISMIC ANALYSIS REPORT THE DOCUMENT SHOULD INCLUDE THE FOLLOWING NEK SPECIFIC DATA: NPP KRŠKO PURCHASE ORDER NUMBER, NPP KRŠKO TECH.(EQUIPM.)SPEC. NUMBER, EQUIPMENT ID (TAG)NUMBER.. X002 - CERTIFICATE OF COMPLIANCE WITH TECHNICAL SPECIFICATION SUPPLIER SHALL CERTIFY THAT THE SUPPLIED VALVES ARE IN COMPLIANCE WITH TECHNICAL SPECIFICATION SP-G508-044687-000, REV.3.. X04 - ASME CODE REQUIREMENTS ASME SECTION III ITEMS SHALL MEET: CLASS 3 CODE EDITION:1971 ADDENDA: WINTER 1972 MATERIAL FOR ITEMS GOVERNED BY THE RULES OF ASME SECTION III MAY BE SUPPLIED TO A LATER CODE EDITION OR ADDENDA PROVIDED THAT ALL THE REQUIREMENTS OF THE ORIGINAL CODE EDITION AND ADDENDA OF ASME SECTION II AND III AND NEK SPECIFIED CODE CASE(S) ARE MET AND THE MATERIAL IS CERTIFIED ACCORDINGLY. IN ADDITION, THE SUPPLIER SHALL PROVIDE NEK WITH A STATEMENT OF CODE RECONCILIATION, IF REQUIRED.. X13 -INSPECTION WITNESS / HOLD POINT NOTIFICATION THE SUPPLIER SHALL PROVIDE ACCESS TO THE SUPPLIER'S PLANT FACILITIES AND RECORDS PERTAINING TO THIS PURCHASE ORDER FOR THE PURPOSE OF PERFORMING INSPECTION ACTIVITES IN ACCORDANCE WITH THE PLAN. NPP KRSKO REQUIRES 21 DAYS ADVANCE NOTICE THAT WITNESS OR HOLD POINTS HAVE BEEN REACHED.. X19 - ADDITIONAL NOTES SEISMIC QUALIFICATION DATA- FLOOR RESPONSE SPECTRA CURVES: - HORIZONTAL OBE- FIGURE A37, - VERTICAL OBE- FIGURE A38, - HORIZONTAL SSE- FIGURE A39, - VERTICAL SSE- FIGURE A40. Copy od Seismic analysis, design report and valve drawing shall be send for review 8 (eight) weeks after receipt of signed purchase order....

4. COMMERCIAL TERMS AND CONDITIONS

4.1 PRICE Total Value of this Purchase Order is: ______________________________ EUR / USD.

4.2 PAYMENT TERMS 30 DAYS after receipt of goods in NPP Krško Purchaser and Seller agree that Seller must issue, and Purchaser must accept and process, e-invoices conforming to the European standard on electronic invoicing provided in the Directive 2014/55/EU of the European Parliament. Purchaser will accept e-invoices to one of his bank accounts: # SI56 0400 1004 8892 548, BIC: KBMASI2X at OTP banka d. d.,1000 Ljubljana; # SI56 0292 4001 8793 453, BIC: LJBASI2X at Nova Ljubljanska banka d.d., Ljubljana; # SI56 3400 0102 2600 457, BIC: KSPKSI22XXX at Banka Sparkasse d. d., Ljubljana. Exceptionally, when Seller is unable to issue electronic invoices compliant with the European standard on electronic invoicing, as provided in the Directive 2014/55/EU of the European Parliament, Seller may issue a PDF invoice and send it to invoices@nek.si.

4.3 INVOICING Original Invoice addressed to NPP Krško should contain the following: - Purchase order number - NPP Krško identification/V.A.T. number: SI61082597 - Description of goods, quantities, unit and total prices and currency - Bank details: supplier’s business bank address, IBAN number, SWIFT (BIC) number and ID number (VAT number) (Europe) or ABA (Routing number), Account number and SWIFT (BIC) number (USA). - TARIC (CUSTOMS) CODE - NET WEIGHT - CLAIMS: Claims, if any, shall be filed within 30-day period - Reference to the Purchase order number This is important as the invoices that cannot be matched will not be paid. The shipment must be furnished with Invoice specifying the description of goods, quantities, unit prices and total prices. Please make sure that your shipping invoice contains customs tariffs for each item in accordance with Brussels Customs Nomenclature.

4.4 DELIVERY TERMS DAP - NPP Krško

4.5 WARRANTY SELLER warrants that all the Hardware furnished under the Purchase Order shall be new and free from liens, encumbrances and defects in title and shall be free from defects in design, workmanship and material and shall achieve the performance and functional requirements as stipulated in NEK Technical and Quality Requirements in section 2 in the Purchase Order. Approval of material, test results, suppliers and schedules by PURCHASER shall not in any way limit or diminish the SELLER’s warranties hereunder. The warranty mentioned in above shall be for the period of two (2) years after PURCHASER’s acceptance of the Hardware delivered under this Purchase Order. SELLER shall remedy at his own cost all faults and hardware and software deficiencies other than normal wear and tear or faults or deficiencies not attributable to PURCHASER detected and reported in writing claim to SELLER by PURCHASER provided that such PURCHASER’s claim has been received by SELLER within the warranty period. The reporting shall be made within thirty (30) days after the detection of the fault or deficiency. The remedy shall be made by (i) replacement or repair of the faulty or deficient unit (spare part or equipment) at SELLER’s option approved by PURCHASER, such approval being not unreasonably withheld, and within shortest reasonable period of time to be determined between the Parties. SELLER’s obligations to remedy faults or deficiencies under the warranty shall be deemed to have been fulfilled when SELLER has either made the remedy at the Site or delivered and installed the replacement unit to PURCHASER and PUCHASER has inspected and accepted it. A refusal shall be for justified reasons only. SELLER shall pay the transportation and insurance cost from Krško Site to the designated facility and back to DAP Krško Site

4.6 INSURANCE AND INDEMNITY PURCHASER represents that it is the responsible operator of the Plant. Therefore, in no event and under no circumstances shall SELLER, its subcontractor, suppliers, directors, agents and the personnel employed by any of them, (hereinafter collectively referred to as the “Indemnified Parties”), irrespective of their activities under this Contract be considered as being the nuclear operator of the Krško Nuclear Power Plant. PURCHASER has in effect and shall maintain in force Material Damage Insurance Policy including machinery break down covering also nuclear and fire perils, and Third Party Liability Insurance Policy against liability and risks arising out of or resulting from a Nuclear Incident (as defined in the Convention on Third Party Liability in the Field of Nuclear Energy of 29th July 1960, as amended by the Additional Protocol of 28th January 1964 and by the Protocol of 16th November 1982 - the Paris Convention) provided in accordance with Slovenian Nuclear Liability Legislation and available within the Slovenian Insurance Market. The indemnified Parties as defined in the above paragraph shall in no event be liable with respect to loss, damage to property and/or injury (including death), caused by or resulting from a Nuclear Incident and PURCHASER shall indemnify, hold harmless and waive all claims and rights of recourse against SELLER

4.7 LIABILITY The total and cumulative liability of the SELLER, including any claim, warranty, cost and expenses of any kind arising out of or resulting from any cause whatsoever, whether based on contract, tort (including negligence), strict liability or otherwise shall in no event exceed 100% of Total Contract Price. In no event and under no circumstances shall SELLER and PURCHASER be liable for any special, incidental, indirect or consequential losses or damage of any nature including but not limited to costs of capital, loss of profits or revenues or loss of use thereof, arising at any time, whether fond on contract, tort (including negligence), strict liability or otherwise. The limitations under this Article shall not apply for damages which are caused wilfully or by gross negligence on the part of SELLER, its subcontractors and all their directors, officers, agents, servants and employees. SELLER shall only be liable for damages occurring up to the end of the pertinent Warranty Period if such damages are reported to the SELLER immediately after occurrence or discovery of the damage. The provisions of this Article 4.7 shall apply notwithstanding any other provisions of this Contract or of any purchase order or other agreement.

You are kindly requested to acknowledge the acceptance of this Purchase Order and confirm the delivery date of items and submittal of requested documentation as stated below each item. Sincerely,. Buyer..